- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

TITLE: Draft ExTAG Decision Sheet – Evaluation of relevant temperatures for EPL Da, Db and Dc

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

This document ExTAG/367 /CD Draft ExTAG Decision Sheet - Evaluation of relevant temperatures for EPL Da, Db and Dc has been prepared by SP Technical Research Institute of Sweden for comment.

Please submit comments using the attached comments table by -

2015 06 19 to

Christine Kane

In the absence of comments the document will proceed for publication.

On behalf of Mr. Gauthier

- Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

| Member Body | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observations To be completed by the originator |
| --- | --- | --- | --- | --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-0:2011 IEC 60079-31:2008 IEC 60079-31:2013 IEC 60079-18:2014 IEC 60079-11:2011 | Clause: Various |  |
| --- | --- | --- |
| Subject: Evaluation of relevant temperatures for EPL Da, Db and Dc Status of document: Draft | Key words: - Temperature under layer of dust | Date: 2015 05 Originator of proposal: SP Technical Research Institute of Sweden TC/SC involved: |
| Question: Is it necessary to considerer dust layer when other temperatures than maximum surface temperature are evaluated for Ex Components and equipment, for EPL Da, and for EPL Db and Dc evaluated with a dust layer? Answer: Yes, dust layer shall be considered for all temperatures relevant for the specific type of Ex protection including: - service temperatures - temperature of compound - temperature of cementing - operating temperatures for pre certified Ex components and equipment Based on this, the following applies: When the standards for a specific type of explosion protection requires a dust layer to be considered for measurement of maximum surface temperature, such a dust layer shall be considered also for evaluation of other relevant temperatures. Justification: For EPL Da it is clearly expressed in IEC 60079-31 (both edition 1 and 2) and in IEC 60079-18 (ed. 4) that maximum surface temperature shall be measured with the equipment surrounded by a layer of dust. For Group III in general, the maximum surface temperature may be determined for a given depth of dust layer surrounding the equipment, according to section 5.3.2.3.2 in IEC 60079-0. Section 5.2 in IEC 60079-0 requires service temperature testing according to section 26.5.1. Section 26.5.1 requires Group III equipment - which shall be evaluated with a dust layer - to be tested surrounded with dust. Furthermore, the maximum rated source of heating or cooling shall be considered for service temperature according to 5.2, which could be understood as that dust layers shall be taken into account. If equipment is allowed to be covered by a layer of dust when used as intended, it is reasonable to consider the layer of dust not only when evaluating the maximum surface temperature but also when evaluating the other relevant temperatures. |  |  |