- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Circulated to: ExTAG – IECEx Testing and Assessment Group

TITLE: Draft ExTAG Decision Sheet – Clarification on the applicability of terminal insulating material test.

INTRODUCTION

This Draft Decision Sheet has been prepared by LCIE.

The standard IEC 60079-7 may be understood in different ways regarding requirements for field wiring connections which are not terminals complying with IEC 60947-7-1, IEC 60947-7-2, IEC 60999-1, or IEC 60999-2. Especially, the applicability of clause 6.9 is often discussed.

This document is issued for a 4 week comment period.

Please submit comments using the attached comments table by-

2015 03 06 to

Christine Kane

If no comments are received the document will proceed for publication.

On behalf of Mr. Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@lcie.fr |
| --- | --- |

| Member Body | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation |
| --- | --- | --- | --- | --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-7:2007 | Clauses: 4.2.2.3 6.9 |  |
| --- | --- | --- |
| Subject: Applicability of terminal insulating material test. Status of document: Draft | Key words: Field wiring connections. Terminal insulating material test. | # Date: # January 2015 Originator of proposal: LCIE |
| Background: Questions are often raised about applicability to increased safety field wiring connecting device of terminal insulation material test, as specified in clause 6.9 of the standard IEC 60079-7:2007. The following drawing is an example of connecting device, not compliant to IEC 60947-7-1, IEC 60947-7-2 or IEC 60999-2, which is designed to be used with cable lugs and includes non-metallic insulating part. Question: Shall any connecting device intended for field wiring which includes non-metallic part (except glass and ceramic materials) be submitted to terminal insulating material test? Answer: Yes, in order to ensure that : - Conductors do not become dislodged from the clamping unit - terminal assembly is not separate from the terminal insulator - terminal insulator does not crack Indeed, clause 4.2.2.3 dedicated to field wiring connection facilities, requires meeting the requirements of 4.2.2.2 where applicable. In case of non-metallic material part, the terminal insulating material test required by clause 4.2.2.2 becomes applicable. |  |  |