INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE

IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Circulated to: ExTAG – IECEx Testing and Assessment Group

TITLE: Draft Decision Sheet - A decision is required from the IECEx to confirm or negate the locked rotor test as a mandatory requirement in IEC 60079-19.

INTRODUCTION

This updated draft was prepared as a result of discussions held during the 2011 ExTAG Split meeting and is now issued for a 2 week comment period.

If no comment is received the document will then proceed for publication.

Comment to forwarded by 2011 09 21 to

Christine Kane

On behalf of Mr. Brenon

## Michel Brenon

ExTAG Secretary

| Address: IECEx Secretariat 286 Sussex Street Sydney NSW 2000 Australia | Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 E-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

| Member Body/ Country | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation |
| --- | --- | --- | --- | --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: Standard IEC60079-19:2006 | Clauses: 5.2.6.3.2, 7.2.6.3.2, 8.2.6.3.2, 9.2.6.3.2 & 11.2.5.2.2 |  |
| --- | --- | --- |
| Subject: Locked rotor test for rewound rotating machines Status of document: Draft | Key words: Locked rotor test | # Date: Revised July 2011 Originator of proposal: GB |
| Question: Is it obligatory to conduct the locked rotor test given as item b) in the following clauses of IEC 60079-19:2006 5.2.6.3.2 7.2.6.3.2 8.2.6.3.2 9.2.6.3.2 11.2.5.2.2 Answer: No The equivalent clause in the latest version of this standard (IEC 60079-19:2010) shall be used for interpretation of these clauses. e.g.: 5.2.6.3.2.b b) The stator windings of cage machines shall be energized at an appropriate reduced voltage, with the rotor locked, to obtain between 75 % and 125 % of full-load current and to check balance on all phases. (The test, which in some respects is an alternative to a full-load test, is used to confirm the integrity of the stator winding and its connections and to indicate the presence of rotor defects.) Unbalance shall be less than 5 % of middle value. NOTE 2 Where this test is not reasonably practical other means of verification should be used. Clause Number IEC 60079-19:2006 Equivalent Clause Number IEC 60079-19:2010 5.2.6.3.2.b 5.2.6.3.2.b 7.2.6.3.2.b 7.2.6.3.2.b 8.2.6.3.2.b 8.2.6.3.2.b 2nd Para 9.2.6.3.2.b 9.2.6.3.2.b 11.2.5.2.2.b 11.2.6.3.2.b |  |  |