INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE

IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Circulated to: ExTAG – IECEx Testing and Assessment Group

TITLE: Review of IECEx TAG DS pertaining to IEC 60079-11

INTRODUCTION

This document, prepared by Mr Ajay Maira, AU, Convenor of Maintenance Team, MT 60079-11, is a result of discussions held during the MT meeting in Windsor in March 2009.

The document has been issued for discussion/consideration during the upcoming ExTAG Meeting to be held in Melbourne, September 2009.

Mr Maira will introduce the topic during the meeting.

## Michel Brenon

ExTAG Secretary

| Address: IECEx Secretariat 286 Sussex Street Sydney NSW 2000 Australia | Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 E-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

Review of IECEx TAG DS pertaining to IEC 60079-11

Review took place at MT 60079-11 meeting in Windsor - March 2009

| Decision sheet | Standard | Title of decision sheet | Contents in brief | Do we still need it now? |
| --- | --- | --- | --- | --- |
| ExTAG DS 2002/001A | IEC 60079-11:1999-02 | Electrochemical sensors | Voltages and currents from such sensors | Retain. Useful information. |
| ExTAG DS 2002/003 | - IEC60079-11: 1999-02 | Rating of components for - Component rating Date: 2002-10-21 battery chargeable Originator of proposal: equipment | - Component rating to consider battery charger voltage | Added to CDV of 6th Edition. Retain till 7th Ed is published. |
| ExTAG DS 2002/004 | #### IEC 60079-11: 1999-02 | - Electrolyte leakage from - cells and batteries | - What if leakage occurs during short circuit test | Added to CDV of 6th Edition. Retain till 7th Ed is published. |
| ExTAG DS 2002/005 | - lEC 60079-11:1999-02 | - Separate voltage sources | - Addition of such sources | No. Adequately covered by rules of intrinsic safety. |
| ExTAG DS 2002/006 | - IEC60079-11: 1999-02 | Rating of components | - Rating of components when in installed condition | Yes. This is a useful guidance. DE to come up with a note to add this information to the CDV of 6th Edition. |
| ExTAG/DS 2003/001A | #### IEC 60079-11 | Limitation of RF power | - How much power is allowable | No. The information is at variance to IEC 60079-0 2007 edition |
| ExTAG DS 2003/003 | - IEC 60079-11 | Assessment of infallible safety shunt assemblies | - Duplicated shunt zeners are infallible | Adequately covered in 2006 edition (5th). Retain till 6th Ed is published. |
| ExTAG DS 2004/002 | - IEC 60079-11: 1999 | Electrochemical cells | - Testing of cells and batteries | Added to CDV of 6th Edition. Retain till 7th Ed is published. |
| ExTAG DS 2004/003 | #### IEC 60079-11 | Use of temperature coefficient for ambient temperatures above 40C | - Does Uo change with ambient temperature above 40? | Text of 2006 edition (5th) addresses this. Retain till 6th Ed is published. |
| ExTAG DS 2004/004 | - lEC 60079-11: - 1999-02 | - Segregation distances where earthed metal separates IS from Non IS circuits. | - Information of where creepage and clearance are considered when earthed tracks and partitions are provided | Added to CDV of 6th Edition. Retain till 7th Ed is published. |
| ExTAG 2006/003 | #### IEC 60079-11 | Galvanically separating components | - Requirements of opto-isolating devices | Text of 2006 edition (5th) addresses this. Retain till 6th Ed is published. |
| ExTAG DS 2006/006 | #### IEC 60079-11: 1999 | Method of test for electrochemical cells | - For how long should battery short circuit test be continued | No. This is a useful guidance, but not necessary to add in Standard, as it is just a logical test technique. |
| ExTAG DS 2006/008 | - lEC 60079-11: - 1999-02 - lEC 60079-11:200x Ed 5 | - Blocking Capacitors | - Rating requirements and a.c. energy transmitted | Text of 2006 edition (5th) addresses this. Retain till 6th Ed is published. |
| ExTAG DS 148CD | - lEC 60079-11:1999-02 - lEC 60079-11:2006 Ed 5 | - Series voltage limiting circuit | - Is it [ia] output if using a series voltage limiting circuit followed by current limiting resistor | No. This is not in compliance with the Standard Clauses 7.5.2 and also 7.5.3 for [ia]. Can only be used for [ib]. |