INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Circulated to: ExTAG – IECEx Testing and Assessment Group

TITLE:  Compilation of comments and observations on ExTAG/341A/CD - Draft ExTAG Decision Sheet –Application of clause 9.2 Dielectric strength test of IEC 60079-18:2009

INTRODUCTION

This document is a compilation of comments, as well as observations from the originator, PTB, DE, on ExTAG/341A/CD - Draft ExTAG Decision Sheet –Application of clause 9.2 Dielectric strength test of IEC 60079-18:2009

This document has been issued for consideration during the ExTAG Christchurch Meeting.

On behalf of Mr. Gauthier

- Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

| Member Body | Clause/ Sub-clause | Paragraph Figure/ Table |  | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CESI - IT |  |  |  | G | Answer is to much generic Scope of application of the answer should be limited or better defined. The application to be limited to low voltage equipment up to 1000Vrms. In the high voltage field of few kV, we should also consider the potential risk of partial discharge which is much sensitive in case of casting or encapsulated process made by polymers. Industrial Standard normally require routine test in case of casting material to insulate circuits. Application only when evidence is available through destructive test (DT) or non-destructive test (NDT) that requirement in 9.1 of IEC 60079-18 has been confirmed. | Answer Provided that equipment under verification is limited to 1000Vrms and the special process of compound (polymerization) is under control…… | Scope limited to voltages up to 1000 Vrms and compound application is under control seems to be reasonable |
| CML |  |  |  |  | The answer is a reasonable justification for waiving the test. The ExTL should decide if the test is not necessary and record the details in the ExTR | Add at the end of the answer: The ExTL shall record the justification for not carrying out the routine test in the ExTR. | Accepted, see CESI - IT |
| DEKRA Certifi-cation B.V. |  |  |  | G | We agree with this sheet |  | noted |
| FME GB |  |  |  | Technical | Although we agree in principle to this change it cannot be implemented by an ExTAG DS. IEC 60079-18 states that “For circuits, which are accessible from the exterior the dielectric strength test shall be used to test the isolation of circuits from each other and from their environment. The test shall be carried out on these circuits in accordance with 8.2.4.” | This draft ExTAG DS is introducing a technical change to IEC 60079-18 which is not permitted by this means. Refer to IEC TC31 MT 60079-18 and request an amendment to the standard. | In IEC 60079-0 it is stated for type tests: 26.1 General “The prototypes or samples shall be tested in accordance with the requirements for type tests of this standard and of the specific standards for the types of protection concerned. However, certain tests judged to be unnecessary, may be omitted from the testing programme. A record shall be made of all tests carried out and of the justification for those omitted.” For routine tests, this statement is not repeated, but it seems reasonable to adopt a similar approach also for routine tests. If this is addressed in a DS it is trested in the same way in all ExTLs |
| FMG (US) |  |  | te |  | We do not support the Decision Sheet as drafted. Although we agree in principle to the proposal change in test protocol, it cannot be implemented by an ExTAG DS. | This draft ExTAG DS is introducing a technical change to IEC 60079-18 which is not permitted by a DS. Stating in a DS that strict compliance is not required would be a technical change to the standard, not an interpretation of an existing requirement. The third paragraph of the “Background” confirms that this is understood. Refer this topic to TC31/MT 60079-18 for an amendment to Edition 4 or as a proposal for Edition 5. | See above for FME GB |
| Kiwa Nederland B.V. (Unit ExVision) |  |  | G |  | Kiwa agrees with the issue of this IECEx ExTAG Decision sheet without comments |  | noted |
| NANIO/ CCVE RU |  |  |  | General | We support ExTAG/341A/CD without any comments. |  | noted |
| NEPSI CN |  |  |  |  | NEPSI supports the draft decisions |  | noted |