INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

Title: 	Compilation of comments and observations on ExTAG/259/CD Draft Decision 	Sheet 	- Inclusion of an IP rating as part of the marking and certificate

Circulation to: ExTAG Members

##### Introduction

This document is a compilation of comments and observations received on ExTAG/259/CD Draft Decision Sheet - Inclusion of an IP rating as part of the marking and certificate.

ExTAG Decision Sheet DS 2012/005 Inclusion of an IP rating as part of the marking and certificate, has now been published, taking into account these comments and observations, and is available on the IECEx Web Site at-

ExTAG Decision List

Michel Brenon

Michel Brenon

ExTAG Secretary

| Address: Standards Australia Building 286 Sussex Street Sydney NSW 2000 Australia | IECEx Secretariat Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 e-mail: chris.agius@iecex.com http://www.iecex.com | Mr Michel Brenon LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 Email: michel.brenon@lcie.fr |
| --- | --- | --- |

| Member Body/ Country | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation |
| --- | --- | --- | --- | --- | --- | --- |
| QPS/ Canada | Overall | ALL | General | QPS supports the subject document as written. | None | Noted |
| NANIO CCVE RU |  |  | General | We support this draft decision sheet in general. It should be noted that IP for rotating electrical machines is determined according to IEC 60034-5, not IEC 60529. |  | Concur. DS revised to reference IEC 60034-5 as well as IEC 60529. |
| UL/DEMKO DK |  | 6 | T | The proposed text will mix Ex based compliance information with non-Ex based compliance information. Adding the non-Ex based IP rating to the Ex-based markings will lead users to believe that the stated IP rating (on the front of the certificate) was obtained in accordance with the Ex standards (also stated on that same front page of the certificate). Based on the fact that the IP rating is decisively depending on having tested with or without Ex-based pretesting, the non-Ex based IP rating shall under no circumstances be assumed to be Ex based. Therefore Ex based markings shall not be mixed with non-Ex based markings at any time. | Replace the text: Compliance with an IP rating in accordance with only IEC 60529 allows for optional (but not mandatory) inclusion of this associated IP rating as part of both the marking and certificate. With the text: The Ex-based markings is shall only include the Ex-based IP rating (if so chosen by the manufacturer). The non- Ex based IP rating can be marked on the labels, but only if clearly separated from the Ex-based markings. In the Ex certificate, the non-Ex based IP rating can be stated under additional information, but not as part of the Ex marking. | This draft Decision Sheet does not introduce a new practice regarding IECEx test reports and certificates. It merely clarifies existing practice. At present, not all types of protection require the same pre-testing from Part 0 depending upon the edition used, with “i” not always requiring any pre-testing from Part 0 at all. As such, the indication of an IP rating in association with an Ex evaluation does not carry any broader indication of testing to the user other than what the IP rating indicates according to IEC 60529 (which is referenced by Part 0). Therefore, no changes to current practice are necessary. |