INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

Title: 	Compilation of comments on ExTAG/196C/CD Draft ExTAG Draft Decision Sheet - A decision is required from the IECEx to confirm or negate the locked rotor test as a mandatory requirement in IEC 60079-19.

Circulation to: ExTAG Members

##### Introduction

This document is a compilation of comments received on ExTAG/196C/CD Draft ExTAG

Draft Decision Sheet - A decision is required from the IECEx to confirm or negate the locked rotor test as a mandatory requirement in IEC 60079-19.

As a result of comment received the ExTAG Decision Sheet DS 2012/002 has now been published on the IECEx Web Site.

Michel Brenon

Michel Brenon

ExTAG Secretary

| Address: Standards Australia Building 286 Sussex Street Sydney NSW 2000 Australia | IECEx Secretariat Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 e-mail: chris.agius@iecex.com http://www.iecex.com | Mr Michel Brenon LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 Email: michel.brenon@lcie.fr |
| --- | --- | --- |

| Member Body/ Country | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation |
| --- | --- | --- | --- | --- | --- | --- |
| Ex-Agencija (HR) |  |  |  | Ex-Agencija support the Decision Sheet ExTAG/196C/CD. |  |  |
| NANIO CCVE RU |  |  | General | The stator winding tests with the locked rotor are the alternative to full-load tests. For some types of production, such as increased safety “e”, type of protection “nA” such tests are critical to ensure explosion safety. | We propose to add the following note of clarification: For the type of protection increased safety “e” and type of protection “nA” stator windings tests with the locked rotor are obligatory. Service facility shall have the required means to repair and test such electrical equipment. | Proposal not accepted The reason for the locked rotor test in all the rotating machine requirements of IEC 60079-19 is to verify the condition of the stator and rotor windings and nothing to do the explosion protection type requirements A locked rotor test for Ex e is required by IEC 60079-19 Clause 8.2.6.1.1 when a rewind is conducted as a copy rewind and the Te time can not be reduced to 75%. |
| UL (US) | 5.2.6.3.2, 7.2.6.3.2, 8.2.6.3.2, 9.2.6.3.2 & 11.2.5.2.2 |  | General | We support ExTAG/196C/CD with the following observation. |  | If the locked rotor test is omitted or other tests and/or techniques as listed are used to verify the integrity of the rotor winding, the polarity of the coils, and the integrity of the stator connections, then a statement shall be included indicating such in the job report to the user, as required under Clause 4.4.1.1. Comment not accepted. This is already a requirement in the 4th paragraph of Clause 4.4.1.1 where the user has to agree to scope of work and the certification status before commencement of work and this has to include a justification of the omission of any test the user could assume to be included. If US want to pursue this they need to take this up with IEC60079-19 maintenance team |