| Reference No: |  |  |  |  |  |  |  |  |  |  | #### IEC 60079-7 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ## Field of application This form is intended to be used when assessing and testing electrical apparatus for explosive atmospheres according to the standard specified in the adjoining column. The test results are valid for the tested items only. Reproduction This report must not be reproduced other than in its entirety except with the prior written approval of the issuing body | Standard: # IEC 60079-7: 1990 Electrical apparatus for explosive gas atmospheres – Increased safety "e" |  |  |  |  | ## Instructions for use The comment columns can be used to e.g. specify test values, applied alternative requirements/tests or to refer to enclosed additional pages with comments. Abbreviations: N/A = Not applicable (for the assessment/test of the equipment and its design documentation) The applicant is the body/person who has requested the assessment/test and to which the results, as specified in this report, are provided. The short descriptions in the column for "Clause" do not replace the complete text in the standard. |  |  |  |  |  |
|  | Amendments: 1 : 1991-04 2 : 1993-04 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | # This test report may only be used for the # IECEx Scheme and must be accompanied by an ExTR cover page issued by an ExCB. |  |  |  |  |  |
| ## Product name |  |  |  |  | # Model/Type designation |  |  |  |  |  |  |
| Serial No | Code (e.g. Ex II T ) |  |  |  |  |  | Ambient temperature [min-max] |  |  |  |  |
| Applicant [name and postal address] |  |  |  |  | Manufactured by [name and postal address] |  |  |  |  |  |  |
| Test sample received [date] |  |  |  |  |  |  |  |  |  |  |  |
| ## Product description |  |  |  |  |  |  |  |  |  |  |  |
| The equipment complies with the standard [yes/no] | ## Prepared by |  |  |  |  |  |  |  |  | Date [year-month-day] |  |
|  | [signature] |  |  |  |  |  |  |  |  |  |  |

Sheet 1 of 57

| Reference No: |  |  |  |  |  |  | IEC 60079-7 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 1 | Scope |  |  |  |  |  |  |  |
| 2 See also DS 2010/006A | Normative references |  |  |  |  |  |  |  |
| 3 | Definitions |  |  |  |  |  |  |  |
| 4 | Constructional requirements for all electrical apparatus |  |  |  |  |  |  |  |
| 4.1 | Terminals for external connections |  |  |  |  |  |  |  |
| 4.2 | Internal connections |  |  |  |  |  |  |  |
| 4.3 | Clearances |  |  |  |  |  |  |  |
| 4.4 | Creepage distances |  |  |  |  |  |  |  |
| 4.5 | Solid electrical insulating materials |  |  |  |  |  |  |  |
| 4.6 | Windings |  |  |  |  |  |  |  |
| 4.7 | Limiting temperature |  |  |  |  |  |  |  |
| 4.8 | Internal wiring |  |  |  |  |  |  |  |
| 4.9 | Degrees of protection provided by enclosures |  |  |  |  |  |  |  |
| 4.10 | Fasteners |  |  |  |  |  |  |  |
| 5 | Supplementary requirements for specific apparatus |  |  |  |  |  |  |  |
| 5.1 | Rotating electrical machines |  |  |  |  |  |  |  |
| 5.1.1 | Degrees of protection by enclosure |  |  |  |  |  |  |  |
| 5.1.2 | Internal fans |  |  |  |  |  |  |  |
| 5.1.3 | Minimum radial air gap |  |  |  |  |  |  |  |
| 5.1.4 | Machines with cage rotors |  |  |  |  |  |  |  |
| 5.2 | Luminaires designed for mains supply |  |  |  |  |  |  |  |
| 5.3 | Cap lamps (except for Group I) and hand lamps with their own source of supply |  |  |  |  |  |  |  |

Sheet 2 of 57

| Reference No: |  |  |  |  |  |  | IEC 60079-7 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 5.4 | Measuring instruments and instrument transformers |  |  |  |  |  |  |  |
| 5.5 | Transformers other than instrument transformers |  |  |  |  |  |  |  |
| 5.6 | Secondary batteries |  |  |  |  |  |  |  |
| 5.6.1 | Battery containers |  |  |  |  |  |  |  |
| 5.6.2 | Cells |  |  |  |  |  |  |  |
| 5.6.3 | Connections |  |  |  |  |  |  |  |
| 5.7 | General purpose connection and junction boxes |  |  |  |  |  |  |  |
| 5.8 | Resistance heating devices and resistance heating units |  |  |  |  |  |  |  |
| 5.9 | Other electrical apparatus |  |  |  |  |  |  |  |
| 6 | Type verifications and type tests |  |  |  |  |  |  |  |
| 6.1 | Electric strength |  |  |  |  |  |  |  |
| 6.2 | Rotating electrical machines |  |  |  |  |  |  |  |
| 6.3 | Luminaires designed for mains supply |  |  |  |  |  |  |  |
| 6.4 | Measuring instruments and instrument transformers |  |  |  |  |  |  |  |
| 6.5 | Transformers other than instrument transformers |  |  |  |  |  |  |  |
| 6.6 | Secondary batteries |  |  |  |  |  |  |  |
| 6.6.1 | Insulation resistance |  |  |  |  |  |  |  |
| 6.6.2 | Shock test |  |  |  |  |  |  |  |
| 6.6.3 | Test for adequate ventilation of battery container |  |  |  |  |  |  |  |
| 6.7 | General purpose connection and junction boxes |  |  |  |  |  |  |  |
| 6.8 | Resistance heating devices and resistance heating units |  |  |  |  |  |  |  |
| 7 | Routine verification and routine tests |  |  |  |  |  |  |  |
| 7.1 | Electric strength test |  |  |  |  |  |  |  |

Sheet 3 of 57

| Reference No: |  |  |  |  |  |  | IEC 60079-7 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 7.2 | Electric strength test (batteries) |  |  |  |  |  |  |  |
| 8 | Marking |  |  |  |  |  |  |  |
|  | Annex A  Lampholders and lamp caps for luminaires designed for mains supply |  |  |  |  |  |  |  |
| A.1 | Test for non-transmission of an internal ignition |  |  |  |  |  |  |  |
| A.2 | Screw lampholders |  |  |  |  |  |  |  |
| A.3 | Lampholders for tubular fluorescent lamps |  |  |  |  |  |  |  |
| A.4 | Other lampholders |  |  |  |  |  |  |  |
|  | Annex B  Cage motors – Methods of test and of calculation |  |  |  |  |  |  |  |
| B.1 | Temperature rise of stator and rotor windings in rated service |  |  |  |  |  |  |  |
| B.2 | Temperature rise in stalled motors (determined experimentally) |  |  |  |  |  |  |  |
| B.3 | Temperature rise in stalled motors (calculated) |  |  |  |  |  |  |  |
| B.4 | Determination of time tE |  |  |  |  |  |  |  |
| B.5 | Motors designed for arduous starting conditions or provided with special protective devices |  |  |  |  |  |  |  |
| B.6 | Motors forming units with converters |  |  |  |  |  |  |  |
|  | Annex C  Type tests for specific forms of resistance heating devices or resistance heating units |  |  |  |  |  |  |  |
| C.1 | Resistance heating devices subject to mechanical stresses |  |  |  |  |  |  |  |
| C.2 | Resistance heating devices or units intended for immersion |  |  |  |  |  |  |  |
| C.3 | Resistance heating devices or units having hygroscopic insulating material |  |  |  |  |  |  |  |
| C.4 | Verification of limiting temperature |  |  |  |  |  |  |  |

Sheet 4 of 57

| Section 2 EVALUATION RECORD To be completed by ExTL IEC 60079-7 (Plus Amendments 1 and 2) Electrical apparatus for explosive gas atmospheres - Part 7: Increased safety 'e' |  |
| --- | --- |
| Report |  |
| Reference No. |  |
| Tested by ( + signature) Approved by (+ signature) Date of issue Content |  |
| This report is based on a standard format prepared by CSA International |  |
| Client |  |
| Name Address |  |
| Evaluation Record Form No. ExTR600797/Version 1a/DS Copyright reserved to the bodies participating in the IECEx Scheme |  |
| Testing laboratory |  |
| Name Address Testing location |  |
| Test item Standard IEC 60079-7 Description. Trademark. Model and/or type reference Manufacturer |  |

Sheet 5 of 57

| Test Item (continued) Rating(s) Type of transformers (where relevant) Application Protection index Other characteristics Rated ambient temperature ta (OC) | stationary / portable / hand-held IP |
| --- | --- |
| Other information |  |

Sheet 6 of 57

General remarks This evaluation record is not valid unless appended to an IECEx Test Report issued by an ExCB, in accordance with IECEx 02. This evaluation record shall not be reproduced except in full without the written approval of the testing laboratory. The test results presented in this evaluation record relate only to the item tested.

Copy of marking plate

Sheet 7 of 57

| MANUFACTURER'S DOCUMENTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Subject | Drawing  | Rev. | Date |

Sheet 8 of 57

Evaluation Record

| IEC 60079-7 |  | COVERAGE 1/2 |  |  |  | # APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  | REQUIREMENTS |  |  |  | YES | NO | ENCL. |  |  |  |
| 1 |  | Scope |  |  |  |  |  |  |  |  |  |
| ### Scope |  |  |  |  |  |  |  |  |  |  |  |
| The electrical apparatus defined below (see overview) and in 2/2 is feasible for coverage in accordance with the specific requirements addressed by this part of IEC 60079: |  |  |  |  |  |  |  |  |  |  |  |
|  | YES (rated voltage; |  |  |  11 kV r.m.s. a.c. or d.c.) |  |  |  |  |  |  |  |
|  | NO |  |  |  |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |  |
| Form sheets included for specific apparatus covered in this report: |  |  |  |  |  |  |  |  |  |  |  |
| SUPPLEMENTARY  SPECIFIC APPARATUS |  |  |  |  | TYPE VERIFICATIONS AND TYPE TESTS |  |  |  | ANNEX |  |  |
| ## Rotating electrical machines |  |  |  |  |  |  |  |  | (normative) |  |  |
|  | 1/16 - - - - - - - - - - - - - - - - - - - - - - - - - - - - - and |  |  |  | 2/10 |  |  |  |  |  |  |
|  | 2/16 (Machines with cage rotors) - - - - - - - - - and |  |  |  | 2/10 - - - - - - - - - - - - - - - - - - - - - and |  |  |  | ## B |  |  |
| ### Luminaires designed for mains supply |  |  |  |  |  |  |  |  |  |  |  |
|  | 3/16 - - - - - - - - - - - - - - - - - - - - - - - - - - - - - and |  |  |  | 3/10 - - - - - - - - - - - - - - - - - - - - - and |  |  |  | ## A |  |  |
| Cap lamps (except for Group I) and hand lamps with their own source of supply |  |  |  |  |  |  |  |  |  |  |  |
|  | 4/16 |  |  |  |  |  |  |  |  |  |  |
| Measuring instruments and instrument transformers |  |  |  |  |  |  |  |  |  |  |  |
|  | 5/16, 6/16 - - - - - - - - - - - - - - - - - - - - - - - - and |  |  |  | 4/10, 5/10 |  |  |  |  |  |  |
| Transformers other than instrument transformers |  |  |  |  |  |  |  |  |  |  |  |
|  | 6/16 - - - - - - - - - - - - - - - - - - - - - - - - - - - - - and |  |  |  | 5/10 |  |  |  |  |  |  |
| Secondary batteries |  |  |  |  |  |  |  |  |  |  |  |
|  | 7/16 through 11/16 - - - - - - - - - - - - - - - - - - and |  |  |  | 6/10, 7/10 |  |  |  |  |  |  |
| General purpose connection and junction boxes |  |  |  |  |  |  |  |  |  |  |  |
|  | 12/16 - - - - - - - - - - - - - - - - - - - - - - - - - - - - and |  |  |  | 8/10 |  |  |  |  |  |  |
| Resistance heating devices and resistance heating units |  |  |  |  |  |  |  |  |  |  |  |
|  | 13/16 through 15/16 - - - - - - - - - - - - - - - - - and |  |  |  | 9/10, 10/10 - - - - - - - - - - - - - - - - and |  |  |  | ## C |  |  |
| Other electrical apparatus |  |  |  |  |  |  |  |  |  |  |  |
|  | 16/16 |  |  |  |  |  |  |  |  |  |  |
| Overview: |  |  |  |  |  |  |  |  |  |  |  |

Sheet 9 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| IEC 60079-7 |  |  |  | ## COVERAGE 2/2 | APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ##### CLAUSE |  |  |  | REQUIREMENTS | YES | NO |  | ENCL. |  |  |
| 2 |  |  |  | Normative references |  |  |  |  |  |  |
| 3 |  |  |  | Definitions |  |  |  |  |  |  |
| Note: The type of protection covered by this part of IEC 60079 is dependent on the specific requirements addressed in the forms which follow. |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |
| ### Normative references |  |  |  |  |  |  |  |  |  |  |
| The electrical apparatus has been assessed to the most recent editions of the standards which are referenced and posted as provisions of this part of IEC 60079: |  |  |  |  |  |  |  |  |  |  |
|  | YES |  |  |  |  |  |  |  |  |  |
|  | NO |  |  |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |
| Definitions |  |  |  |  |  |  |  |  |  |  |
|  | All definitions covered in Clause 3 apply, as noted for the specific requirements herein |  |  |  |  |  |  |  |  |  |
|  | Increased safety "e" does not apply to the following parts/components of the apparatus: |  |  |  |  |  |  |  |  |  |
|  |  | Part or component (details) |  |  |  |  | Type of protection |  |  |  |
| Note: Apparatus producing arcs or sparks in normal service is excluded by the definition of Increased Safety. |  |  |  |  |  |  |  |  |  |  |

Sheet 10 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | CONSTRUCTION  ALL APPARATUS 1/8 |  |  |  |  |  | APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  | YES | NO | ENCL. |  |  |  |  |
| 4.1 |  |  |  | Terminals for external connections |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Terminals for external connections |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The connection means defined below apply to internal connections noted on 2/8 , Page |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Circuit/identification (if applicable, component mfr., part no., certification) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Apparatus rated current (A): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Conductor cross-section (mm2) (ref. IEC 60364-5-523) |  |  |  | required: |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | accommodated: |  |  |  |  |  |  |  |  |  |  |  |
|  | Number/sizes of conductors that can be safely connected; refer to document: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | aSelf-loosening from mounting(s) prevented by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | aConductor slippage from intended location prevented by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a, bMeans ensuring proper contact without damage to conductors: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Means preventing turning, twisting or permanent deformation during normal tightening (tightening torque as defined by manufacturer): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Details of resilient intermediate part included with terminals for clamping stranded conductors: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | cEffective connection for smaller conductor sizes: (mm2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Precautions against vibration and shock (i.e. where necessary): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Precautions against electrolytic corrosion of aluminium parts: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a"Crimped" cable terminations are allowed if requirement is met bIncluding stranded conductors in terminals for direct conductor clamping cTerminals for connecting conductors of cross-sections  4 mm2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Terminals do not have sharp edges which would damage conductors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Contact assured by terminals is not appreciably impaired by temperature changes in normal service |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | see forms for IEC 60079-0 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | other reference: |  |  |  |  |  |  |  |  |  |
|  |  | Contact pressure is not transmitted through insulating material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 11 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  | CONSTRUCTION  ALL APPARATUS 2/8 |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  | REQUIREMENTS |  |  |  |  |  |  | YES |  |  | NO |  | ENCL. |  |  |
| 4.2 |  | Internal connections |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Internal connections |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Circuit/identification (if applicable, component mfr., part no., certification) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Screwed fasteners |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (locking means) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Crimping |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Soldering |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (securing means) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Brazing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Welding |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Aluminium parts |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (precautions against electrolytic corrosion) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| As for external connections |  |  |  | 1/8, Page |  |  |  | 1/8, Page |  |  |  |  | 1/8, Page |  |  |  |
| Note: Connections shall not be subject to undue mechanical stress. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 12 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  | CONSTRUCTION  ALL APPARATUS 3/8 |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  | YES |  | NO |  |  | ENCL. |  |  |  |  |  |
| 4.3 |  |  | Clearances |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Clearances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Between circuit parts: |  |  |  | Working voltage, U (V) highest rated value | Minimum clearance (mm)  3 mm required for external connections |  |  |  | Through-air path (Figure 2) |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Line-of-sight distance (Examples 1, 2, 3, 5, 6, 7) | Interrupted by insulating part |  |  |  | Interrupted by floating part (Example 11) |  |  |
|  |  |  |  |  |  |  |  |  |  | solid or cemented rib (Example 4) |  | barrier (Example 8) | recess or step (Examples 9, 10) |  | no. of air path sections having dimension X  2.5 mm |  |
| No |  |  |  |  | Required |  | Measured |  | (X) | (X) or no. |  | (X) or no. | (X) | (X) or no. |  |  |
| Notes: 1. For required clearances refer to Table 1 (Table A.1 for lamps with screw caps). 2. In the case of a floating part (Example 11), any through-air path section having dimension X  2.5 mm is not counted. 3. Clearance is the minimum value for all possible directions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 13 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | CONSTRUCTION  ALL APPARATUS 4/8 |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  | YES |  |  | NO |  |  | ENCL. |  |  |  |  |  |
| 4.4 |  |  |  | Creepage distances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Creepage distances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Between circuit parts at working voltage, U (refer to, Sheet 3/8, Clearances) | Minimum creepage distance (mm)  3 mm required for external connections |  |  |  | Electrical insulating material |  | Creepage path (Figure 2) |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Line-of-sight distance (Examples 1, 5) |  | Floating part (Example 11) |  |  | Insulation surface profile |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | solid or cemented rib (Example 4)  2.5 mm high,  1.0 mm thick | parallel-sided groove (Examples 2, 6, 7)  2.5 mm deep and 2.5 mm wide |  | V-shaped groove incl. 2.5 mm bottom link (Example 3)  2.5 mm deep and > 2.5 mm wide | barrier (Example 8) | recess or step (Examples 9, 10) |  |  |
|  |  |  |  |  | Material group (I, II, IIIa); ref. Table 2 | Type of material |  |  |  | no. of creepage path sections having dimension X  2.5 mm |  |  |  |  |  |  |  | gap dimension X  2.5 mm |  |
| (No) | Required |  | Measured |  |  |  | (X) |  | (X) or no. |  |  | (X) or no. | (X) or no. |  | (X) or no. | (X) or no. | (X) | (X) |  |
| Notes: 1. For required creepage distances refer to Table 1 (Table A.1 for screw lampholders and lamp screw caps). 2. Creepage distance is the minimum value, following surface contours, in all possible directions. 3. In the case of a floating part (Example 11), any creepage path section having dimension X  2.5 mm is not counted. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 14 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  | CONSTRUCTION  ALL APPARATUS 5/8 |  |  |  | APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  | YES | NO |  | ENCL. |  |  |  |
| 4.5 |  |  | Solid electrical insulating materials |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Solid electrical insulating materials |  |  |  |  |  |  |  |  |  |  |  |  |  |
| refer to Sheet 3/8, Clearances (alternatively, part as defined in next column) | Insulating part |  |  | Where the original surface of plastics or laminates is removed during manufacture: |  |  |  |  |  |  | Temperature |  |  |
|  |  |  |  | Coating not required |  | Insulating varnish coating (material) required if CTI grading is diminished due to removal of original surface |  |  | CTI of coating  value for original surface |  | Maximum value attained in service (C) (refer to forms for IEC 79-0, Temperature measurement) | Rating of material (C) |  |
|  |  |  |  | CTI not affected | specified creepage distance provided by other unaffected parts |  |  |  |  |  |  |  |  |
| (No) |  |  |  | (X) | (X) |  |  |  | (X) |  |  |  |  |
| Required: 80 C  temperature rating of insulating parts  service temperature + 20 K, except temperature rating of insulated windings, internal wiring or permanently connected cables  service temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 15 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  | CONSTRUCTION  ALL APPARATUS 6/8 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES | NO | ENCL. |  |  |
| 4.6 |  |  | Windings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Windings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part/component |  |  |  | nominal conductor diameter  0.25 mm | nominal conductor diameter < 0.25 mm |  | enamelled winding wires + impregnation |  |  | fully insulated high voltage winding coils/conductors |  | Winding insulation (details) |  |  |  |  |  |
|  |  |  |  |  |  | type of protection per IEC 60079-0 other than 'e' |  | Grade 1 winding wire withstanding breakdown voltage for Grade 2 (see Note) | Grade 2 winding wire |  | sub-assembly impregnated, filled etc. |  |  |  |  |  |  |
|  |  |  |  | (X) | (X) |  | (X) | (X) | (X) | (X) | (X) |  |  |  |  |  |  |
| (1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (3) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (4) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (5) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (6) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: For Grade 1 there shall be no failure with the minimum values of breakdown voltage for Grade 2 when tested per Clause 13 of IEC 60317-3, -7 or –8 and not more than six faults per 30 m of wire irrespective of diameter when tested per Clause 14 of IEC 60317-3, -7 or –8. For documentation verifying compliance with these requirements refer to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (3) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (4) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (5) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (6) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 16 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  | CONSTRUCTION  ALL APPARATUS 7/8 |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  |  | YES |  |  | NO |  |  | ENCL. |  |  |  |  |  |  |
| 4.7 |  |  | Limiting temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Limiting temperature |  |  |  | Note: For data confirming compliance with limiting temperatures specified below, refer to forms for IEC 60079-0, Temperature measurement and/or to the applicable forms which follow. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Maximum surface temperature as prescribed by IEC 60079-0: |  |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |  |  |  |
| Each part identified in the table below is subject to the indicated maximum permissible temperature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Apparatus part |  |  |  |  | Maximum permissible temperature i.e. < max. surface temperature as prescribed by IEC 60079-0, based on the most restrictive aspect (C) (*except higher luminaire interior temperatures with lamp surface C limited as noted) |  | Limiting aspects |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Thermal stability |  |  |  |  |  |  | cage rotor, including during starting (300 C) | thermal class (A, E, B, F, H) of insulation (Table 4) for insulated winding (during time tE) |  | measuring instrument/instrument transformer, during passage of Ith (200 C) | Lamp in luminaire (mains supply) |  |  |  |  |
|  |  |  |  |  |  |  |  | insulating material (temperature rating) refer to Sheet 5/8, Solid electrical insulating materials | conductors, metal parts |  |  |  | thermal class (A, E, B, F, H) of insulation (Table 4) for insulated winding (in rated service) |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | limiting aspects of conductors shall account for self-heating and heat from other parts |  |  |  |  |  |  |  |  |  | *highest lamp surface C + 50 K  lowest temperature of ignition (inside luminaire) of the applicable potentially explosive atmosphere | temperature at rim of lamp cap or at soldering point of lamp cap (195 C) | thermal class (A, E, B, F, H) of ballast winding insulation (Table 4, 1 b) - rectifying effect of aging fluorescent lamp |  |  |
|  |  |  |  |  |  |  |  |  | reduction of mechanical strength | mechanical stress due to thermal expansion |  | damage to neighbouring electrical insulating parts |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | (X) | (X) | (X) |  | (X) |  |  | (X) |  |  | (X) | (X) | (X) |  |  |  |
| Specific protective devices ensuring that the limiting temperatures for windings are not exceeded: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Windings of: |  |  |  | Protective device inside/outside electrical apparatus (manufacturer/type/ratings/location/certification or "not required" and reason) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: Protective devices are not required if winding C  limiting value (Table 4) for rated service even when subjected to continuous overload (including stalled condition) or, alternatively, if windings cannot be subjected to overload. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 17 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  | CONSTRUCTION  ALL APPARATUS 8/8 |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  | YES |  |  |  | NO |  |  | ENCL. |  |  |
| 4.8 |  |  |  |  |  | Internal wiring |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.9 |  |  |  |  |  | Degrees of protection provided by enclosures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.10 |  |  |  |  |  | Fasteners |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Internal wiring |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Wiring subject to contact with conductive parts (details including manufacturer, type, rating, certification) |  |  |  |  |  | Contact with conductive parts prevented by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | mechanical protection (method) |  |  |  |  |  |  |  | fixing (method) |  |  |  |  |  |  |  |
| Degrees of protection provided by enclosures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Entire apparatus |  | Apparatus sub-assembly |  |  |  |  | Degree of protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | IP54 (bare conductive parts) | IP44 (insulated conductive parts) | other (higher) degree | rotating machine (Note 2) |  |  | Drainage/ventilation |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | drain hole |  | ventilation opening |  | reduced degree of protection | Manufacturer's documentation covering details (reference) |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | minimum degree excluding terminal boxes & bare parts |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | IP23 (Group I) | IP20 |  |  |  |  |  |  |  |  |  |  |
|  | (X) |  |  |  |  |  |  | (X) | (X) | (IP) | (X) | (X) |  | (X) or no. |  | (X) or no. |  | 'NO' or (IP) |  |  |  |  |
|  | Notes: 1. If drain holes or ventilation openings reduce the degree of protection below IP54 (enclosed bare parts) or IP44 (enclosed insulated parts), the marking shall include the sign "X" and the degree(s) of protection provided by the enclosure. 2. Refer to ROTATING ELECTRICAL MACHINES, Degrees of protection by enclosure. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fasteners |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Group I electrical apparatus: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to forms for IEC 60079-0, Fasteners, Special fasteners |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 18 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 1/16 |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | YES |  |  | NO |  | ENCL. |  |  |  |  |  |  |
| 5.1 |  |  |  |  |  | Rotating electrical machines |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.1.1 |  |  |  |  |  | Degrees of protection by enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.1.2 |  |  |  |  |  | Internal fans |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.1.3 |  |  |  |  |  | Minimum radial air gap |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rotating electrical machines |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Degrees of protection by enclosure (see forms for IEC 60079-0 re ventilation) (ref. CONSTRUCTION  ALL APPARATUS, Degrees of protection by enclosure) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Terminal box/enclosed bare conductive parts: (degree of protection by enclosure, IP |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) Required: IP54 |  |  |  |  |  |
|  |  | refer to forms for IEC 60079-0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Enclosed ventilated machine with pipe connection for cooling air inlet/outlet: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cooling method IC3X (using remote medium) per IEC 60034-6; circulation method 1, 5, 6, 7, 8 ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ); details: |  |  |
| degree of protection by enclosure, IP |  |  |  |  |  |  |  |  |  | Minimum required: IP20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Objective: The enclosure of the apparatus, when installed with suitable ducting, will provide degree of protection IP44. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | the marking includes the sign "X" indicating use only with pipe connections for cooling air inlet/outlet |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: The degree of protection is not required to be marked if all of the above requirements are met. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rotating electrical machine for use only in clean environments; details re use (e.g. manufacturer's instructions): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| degree of protection by enclosure, IP |  |  |  |  |  |  |  |  |  |  | Minimum required: IP23 for Group I; IP20 for Group II |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ref. forms for IEC 60079-0 re means preventing vertical ingress of solid foreign bodies |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | the marking includes the sign "X" indicating use only in clean environments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Note: The (reduced) degree of protection shall be marked. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Internal fans (if provided) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to forms for IEC 60079-0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Minimum radial air gap |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rotor diameter D (mm) 75 minimum 750 maximum |  |  |  | Max. rated speed n (rpm) 1000 minimum |  | Core length (mm) |  |  |  |  | Ratio r (core length  1.75  D) | Factor b |  |  | Radial air gap between stator and rotor |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | rolling bearings (1.0) |  | plain bearings (1.5) | Required ref. formula for minimum value (mm) |  |  |  |  | Actual (mm) |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | (X) |  | (X) |  |  |  |  |  |  |  |  |  |  |

Sheet 19 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 2/16 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES | NO |  | ENCL. |  |  |
| 5.1.4 |  |  |  |  |  | Machines with cage rotors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Machines with cage rotors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Synchronous machine: |  |  |  |  |  |  |  |  |  | rotor starting winding |  |  |  | rotor damping winding |  |  |  |  |  |  |  |
| Bars of cage rotors: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | one-piece bar/ring assembly; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | alternative to one-piece bar/ring assembly, bars are |  |  |  |  |  |  |  |  |  |  | brazed to shorting rings |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | welded to shorting rings |  |  |  |  |  |  |  |
|  |  | bars fitted tightly into core slots, ensuring prevention of sparking during starting; method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Limiting temperature of rotor, |  |  |  |  |  |  |  |  |  |  | C not to exceed 300 C (including during starting) |  |  |  |  |  |  |  |  |  |  |
| (refer to CONSTRUCTION  ALL APPARATUS, 7/8, Limiting temperature and ANNEX B) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Determination of starting current ratio IA/IN and time tE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Rated current IN (A) |  |  |  |  |  | Initial starting current IA determined in ANNEX B (A) |  |  |  |  | Starting current ratio IA/IN Required: ratio  10 |  |  | Time, tE |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | (1) minimum value determined in ANNEX B (s) Required:  5 s |  |  | (2) value given in Figure 7 as a function of IA/IN (s) |  |  |  |
| Compatibility with provision for the selection of a protective device to prevent non-permissible temperatures: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | tE (1) > tE (2); i.e. suitable for protection by a current-dependent device (ref. Annex D) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | tE (1) < tE (2) in which case a suitable overload protective device is used for the machine as proven by test; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - refer to CONSTRUCTION  ALL APPARATUS, Limiting temperature, Specific protective devices………. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | the protective device is identified by marking on the machine (see MARKING) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - for test documentation verifying compliance with maximum permissible temperature, refer to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | winding temperature sensor(s) is associated with protective device proven suitable when machine is stalled; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - refer to CONSTRUCTION  ALL APPARATUS, Limiting temperature, Specific protective devices………. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | protective device is identified by marking on the machine (see MARKING) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - for test documentation verifying compliance with maximum permissible temperature, refer to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Motor supplied at varying frequency/voltage by a converter per (document) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | : |  |
|  |  |  |  | - for test documentation verifying compliance with maximum permissible temperature for the motor together with the converter and in association with the protective device that is provided, refer to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 20 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 3/16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  | NO |  |  |  |  |  | ENCL. |  |  |  |  |  |
| 5.2 |  |  |  | Luminaires designed for mains supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Luminaires designed for mains supply (see also forms for IEC 60079-0) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Light source; manufacturer/part no./certification (number of lamps used, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ): |  |  |  |  |  |  |  |  |  |  |  |  |
|  | cold starting fluorescent lamp with single-pin caps (Fa6) per IEC 61-1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | tungsten filament lamp for general lighting service per IEC 64 and 432 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | blended (MBTF) lamp |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | other lamp type ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ): |
|  |  |  |  |  |  |  |  |  |  | light source |  |  |  | parts do not attain a higher temperature than the limiting temperature, C, for a period longer than 10 s following breakage of the bulb |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | - temperature at 10 s after bulb breakage, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C at |  |  |  |  |  |  | C ambient |  |  |  |
|  |  |  |  |  |  |  |  |  |  | lamp does not contain free metallic sodium |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Lamps containing free metallic sodium (e.g. low pressure sodium lamps per IEC 60192) are not permissible |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Distance between lamp and protective cover (fluorescent tubes): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | protective lamp compartment cover; distance between lamp and cover, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | mm Required:  5 mm |  |  |  |  |  |  |  |  |  |  |  |
|  | protective cover is an outer tube; distance between lamp and cover, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | mm Required:  2 mm |  |  |  |  |  |  |  |  |  |  |  |
| Distance between lamp and protective cover (other lamps): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - lamp wattage, |  |  |  |  |  |  |  | W; required distance for corresponding lamp wattage, P in Table 5, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | mm |  |
| - actual distance between lamp and cover, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lampholder (manufacturer/part no./ratings/certification): (see ANNEX A) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | edison type, E |  |  |  |  |  | (IEC 60238) |  |  |  |  |  |  |  |  |  |  |  |  |  |  | fluorescent, Fa6 (IEC 60061-2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (other) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Maximum surface temperature inside luminaire (* |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C): (other than lamp surfaces) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  value for T Class per IEC 60079-0 or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | > value for T Class per IEC60079-0 and use is limited to specific potentially explosive atmosphere(s) below |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ), |
| in which case |  |  |  |  |  |  |  |  |  | highest surface temperature of the lamp (* |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C) inside the luminaire |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | is at least 50 K below the lowest temperature of ignition ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C), inside |  |  |
|  |  |  |  |  |  |  |  |  |  | the luminaire, of the explosive atmosphere(s) for which the luminaire is intended |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | (explosive atmosphere ignition temperature derived from (source/test reference): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Note: This dispensation is only valid for the gas atmospheres indicated in the certificate. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature at rim of lamp cap, * |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C; limiting value, |  |  |  |  |  |  |  |  |  |  |  |  |  | C not to exceed 195 C |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature at soldering point of lamp cap, * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C; limiting value, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C not to exceed 195 C |  |  |  |  |  |  |  |  |
| *(refer to forms for IEC 60079-0, Temperature measurement) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ballast for tubular fluorescent lamp; manufacturer/part no./ratings/certification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - maximum temperature, |  |  |  |  |  |  |  |  |  |  | C; limiting value, |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (maximum temperature per TYPE VERIFICATIONS AND TYPE TESTS, Thermal test for luminaires with tubular fluorescent lamps) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 21 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 4/16 |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  | YES |  | NO |  | ENCL. |  |  |  |  |  |  |  |
| 5.3 |  |  |  |  | Cap lamps (except for Group I) and hand lamps with their own source of supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cap lamps (except for Group I) and hand lamps with their own source of supply (see also forms for IEC 60079-0) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Protective cover (material/ over-all dimensions, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ): |  |  |  |
|  |  | minimum distance between cover and lamp with lamp securely inserted, |  |  |  |  |  |  |  |  | mm Required:  1 mm or |  |  |  |  |  |  |  |  |
|  |  | lamp inserted in a spring-loaded lampholder and in contact with protective cover; spring travel, |  |  |  |  |  |  |  |  |  |  |  | mm |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Required spring travel:  3 mm |  |  |  |  |  |  |  |  |  |  |
|  |  | cover guard; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |  |  |
|  |  | area of cover  50 cm2 and cover is protected by a protruding rim with a minimum height of 10 mm; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |  |
|  |  | area of cover > 50 cm2 and cover guard complies with *mechanical test requirements of IEC 60079-0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (*refer to forms for IEC 60079-0, Test for resistance to impact, Enclosure or part of enclosure) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Switching device(s) in the lamp circuit which produce sparks or arcs in normal service; details: Note: Including (e.g.) hermetically-sealed reed switches. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - means preventing contact separation within the hazardous area: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | not required (type of protection per IEC 60079-0 other than 'e', |  |  |  |  |  |  |  |  |  |  |  |  | ) or |  |  |  |  |
|  |  | mechanically interlocked, method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |
|  |  | electrically interlocked, method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 22 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 5/16 |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  | YES |  | NO |  | ENCL. |  |  |  |
| 5.4 |  |  |  | Measuring instruments and instrument transformers |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Measuring instruments and instrument transformers Note: Instruments with moving coils are not permitted. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Device; details (including manufacturer/part no./ratings/certification as applicable): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Continuous withstand: (refer to CONSTRUCTION  ALL APPARATUS, Limiting temperature) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Condition |  |  |  | Duration |  | Temperature |  |  |  |  |  |  |
|  |  |  |  |  | 1.2  rated current | (A) | 1.2  rated voltage | (V) |  |  | Measured |  |  |  | Limiting value (C) |  |  |
|  | a | condition applied to: (circuit) |  |  |  |  |  |  |  |  | Method |  | (C) |  |  |  |  |
|  | b | component/surface/part |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | (X) |  | (X) |  |  |  |  |  |  |  |  |  |  |
|  | a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ambient |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 6/16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 23 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 6/16 |  |  | APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  | YES | NO | ENCL. |  |  |
| 5.4 |  |  |  |  |  | Measuring instruments and instrument transformers (continued) |  |  |  |  |  |  |  |
| 5.5 |  |  |  |  |  | Transformers other than instrument transformers |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Measuring instruments and instrument transformers (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Current transformers and current-carrying parts of measuring instruments: (excluding voltage circuits) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Circuit/condition |  |  | Current (ref. Table 6) |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Isc (measured) (A) | Ith (applicable value)  1.1  Isc (A) |  |  | Idyn (applicable value)  1.25  2.5 Isc (A) |  |  |
|  | No |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: For current-carrying parts supplied by current transformers, the values of Ith and Idyn need only equal the current flowing in the short- circuited secondary windings of the current transformer with its primary windings carrying the currents Ith and Idyn applicable to them. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Refer to TYPE VERIFICATIONS AND TYPE TESTS, Measuring instruments and instrument transformers: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | no reduction in level of security against explosions |  |  |  |  |  |  |  |  |  |  |
|  |  |  | temperatures attained during passage of short-time current Ith do not exceed limiting values in no case > 200C |  |  |  |  |  |  |  |  |  |  |
| Transformers other than instrument transformers |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer/part no./ratings/certification (including any integral or fully-specified protective device): |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | refer to TYPE VERIFICATIONS AND TYPE TESTS, Transformers other than instrument transformers |  |  |  |  |  |  |  |  |  |  |

Sheet 24 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 7/16 |  |  |  |  |  |  | APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  | YES | NO |  | ENCL. |  |
| 5.6 |  |  |  |  | Secondary batteries |  |  |  |  |  |  |  |  |  |  |  |
| 5.6.1 |  |  |  |  | Battery containers |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Secondary batteries (see also forms for IEC 60079-0) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Type: |  |  |  |  |  |  |  | lead-acid |  | nickel-iron |  |  |  | nickel-cadmium |  |  |
| Manufacturer/part no./voltage/ampere-hours/configuration/range of capacities): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: Batteries with capacity > 25 Ah at the 5 h rate are subject to requirements for Battery containers, Cells and Connections following. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Provision for charging; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | charging is intended to be applied outside the hazardous area (see MARKING re warning plate) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | in accordance with manufacturer's instructions |  |  |  |  |  |  |  |  |
|  | charging is intended to be applied in the hazardous area; safety measures: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Battery containers (see Figure 1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Container materials and assembly: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | steel; including (parts): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | other material(s) (parts as noted): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: Materials of construction other than steel are permissible only for Group II. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | internal surfaces of metallic material are lined with a bonded insulating layer; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | cover is painted (alternative to bonded insulating layer); details: |  |  |  |  |  |  |  |  |
|  | electrolyte ( |  |  |  |  |  |  |  |  |  | ) has no adverse affect on internal surfaces |  |  |  |  |  |
|  | design withstands mechanical stresses in use (including transportation/handling) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | ref. forms for IEC 60079-0, Test for resistance to impact |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | ref. forms for IEC 60079-0, Drop test |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | partition walls are incorporated for the purpose; details: |  |  |  |  |  |  |  |  |
| continued on 8/16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 25 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 8/16 |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  | YES | NO |  | ENCL. |  |  |  |
| 5.6.1 |  |  |  |  |  |  |  |  | Battery containers (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Battery containers (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insulating barriers (material/dimensions): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Notes: 1. Construction shall be such that required creepage distance in service is not reduced in an inadmissible way. 2. Surface grooves shall not be considered in the calculation of creepage distances. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | partition wall (ref. 8/16) serves as insulating barrier |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | positioned between |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | height ( |  |  |  |  |  | mm)  2/3 cell height of |  |  |  |  |  | mm |  |  |  |  |  |  |  |  |
|  |  |  |  | prevents development of a nominal voltage exceeding 40 V in any section |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | ref. CONSTRUCTION  ALL APPARATUS, Clearances |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | other purpose; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Creepage distance between poles of adjacent cells and poles and battery container for: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - nominal voltage  24 V; |  |  |  |  |  |  |  |  |  |  35 mm |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - nominal voltage > 24 V; |  |  |  |  |  |  |  |  |  | 35 mm + at least |  |  |  | mm, based on a value of |  |  |  |  | V |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Required:  1mm added for each 2v in excess of 24 V |  |  |  |  |  |  |  |  |  |  |  |
| Cover attachment method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Note: The possibility of inadvertent opening or displacement in service shall be avoided. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | refer to forms for IEC 60079-0, Fasteners |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cell installation: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | means which prevent displacement in service:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | materials/electrolyte resistant properties for terminal mountings:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | and for |  |
|  | built-in items (e.g. packing, insulating barriers) :- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
|  | Note: These insulating materials shall be non-porous and not easily ignitable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Drain holes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | YES; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | NO; means which allow extraction of liquid without cell removal: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ventilation; details of openings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ref. TYPE VERIFICATIONS AND TYPE TESTS, Test for adequate ventilation of battery container |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | hydrogen concentration in the battery container does not exceed 2 % by volume |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 9/16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 26 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 9/16 |  |  |  |  |  | APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  | YES | NO | ENCL. |  |
| 5.6.1 |  |  | Battery containers (continued) |  |  |  |  |  |  |  |  |  |
| 5.6.2 |  |  | Cells |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |
| Battery containers (continued) |  |  |  |  |  |  |  |  |  |  |  |  |
| Plugs and sockets; manufacturer/part no./ratings/pin configuration: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | separation requires the use of a tool; method: |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | ref. forms for IEC 60079-0, Fasteners, Special fasteners |  |  |  |  |  |  |
|  |  |  |  |  |  | warning label, indicating "SEPARATE ONLY IN A NON-HAZARDOUS AREA" |  |  |  |  |  |  |
|  | separation does not require the use of a tool; ref. forms for IEC 60079-0 |  |  |  |  |  |  |  |  |  |  |  |
|  | (single pole plugs and sockets) positive and negative plugs are non-interchangeable; features: |  |  |  |  |  |  |  |  |  |  |  |
| Polarity markings: Note: Detail shall be unambiguous and the method shall be permanent. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | battery; detail/method: |  |  |  |  |  |  |  |  |  |  |  |
|  | plugs and sockets; detail/method: |  |  |  |  |  |  |  |  |  |  |  |
| Other electrical apparatus affixed to/incorporated in battery container: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | type of protection per IEC 60079-0 other than 'e': |  |  |  |  |  |  |  |  |  |  |  |
| Cells (see Figure 1) |  |  |  |  |  |  |  |  |  |  |  |  |
| Cell lid (material: |  |  |  |  |  |  |  | ) Note: Readily ignitable materials shall not be used. |  |  |  |  |
|  | sealed to cell container so as to prevent detachment and electrolyte leakage; method: |  |  |  |  |  |  |  |  |  |  |  |
| Positive and negative plates; method of support: |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 10/16 |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 27 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 10/16 |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | YES | NO | ENCL. |  |  |  |
| 5.6.2 |  |  |  |  | Cells (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.6.3 |  |  |  |  | Connections |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cells (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cells requiring maintenance of electrolyte level: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | means of indicating that the electrolyte level is between minimum and maximum permissible levels: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | precautions against excessive corrosion of plate lugs/busbars with electrolyte at minimum level: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Allowance for expansion of electrolyte and deposition of slurry: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | headspace, |  |  |  |  |  |  |  |  |  | mud space, |  |  |  |  |  |  |  |
|  | spaces are related in volume to anticipated battery life, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Filling and vent plugs: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | easily accessible for maintenance; location/access by |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | design prevents electrolyte ejection in normal use; features: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Terminal post/lid seals; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: Seals shall be electrolyte-tight. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insulation resistance between live parts and battery container: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | measured on new fully charged battery |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  1 M |  |  |  |  |  | < 1 M |  |  |  |  |  |  |  |  |  |  |  |
| ref. TYPE VERIFICATIONS AND TYPE TESTS, Secondary batteries, Insulation resistance for test procedure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Connections |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Intercell connections between adjacent cells which can move relative to one another: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | non-rigid; material/cross-sectional area/shape/insulation of connecting conductor: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | welded into cell terminal post |  |  |  |  |  |  |  |  |  | soldered into cell terminal post |  |  |  |  |  |  |  |
|  | crimped into a copper sleeve cast into terminal post (copper connector required) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | crimped into copper termination screwed by threaded fastener into cell terminal post (copper connector required) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - fastener ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) and |  |  |
|  | - means preventing loosening: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | fastener engages copper insert cast into cell terminal post |  |  |  |  |  |  |  |  |  |  |  |
| continued on 11/16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 28 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 11/16 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES | NO | ENCL. |  |
| 5.6.3 |  |  |  | Connections (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Connections (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | effective contact area ( |  |  |  |  |  |  | mm2) between termination and cell terminal post  connector cross-section |  |  |  |  |  |  |  |  |
|  |  | Note: No account of shall be taken of the area of male and female threads in contact. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ref. forms for IEC 60079-0, Temperature measurement for heating tests of screwed joints at rated connector current |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | rated connector current ( |  |  |  |  |  | A) specified in (document): |  |  |  |  |
| Duty (service) current, |  |  |  |  |  |  |  | A: (Note: Total current considered for single connector where double connectors are used.) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | continuous |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | intermittent (e.g. "on/off" periods); |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | *at the battery manufacturer's discharge rate used to determine battery capacity: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | (Note: *Applied where the duty cannot be defined.) |  |  |  |  |  |  |  |  |  |  |
|  | - maximum connector temperature, |  |  |  |  |  |  |  |  | C when carrying the current required for the duty |  |  |  |  |  |  |  |
|  | (ref. forms for IEC 60079-0, Temperature measurement) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - limiting temperature, |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
| (ref. CONSTRUCTION  ALL APPARATUS, Solid electrical insulating materials and Limiting temperature) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Connectors exposed to attack by electrolyte; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | : |
|  |  | protected by |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (e.g. for lead-acid batteries, non-insulated connectors of metals other than lead shall be lead-coated) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Live parts of Group I battery: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | insulating covering of each live part to avoid tracking currents and accidental contact; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Live parts of Group II battery: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | insulating protection of live parts to avoid accidental contact; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 29 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 12/16 |  |  |  |  | APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  | YES | NO | ENCL. |  |  |  |  |
| 5.7 |  |  |  |  |  |  | General purpose connection and junction boxes |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General purpose connection and junction boxes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Terminal assemblies (manufacturer/part no./ratings/certification): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Permissible maximum dissipating power, |  |  |  |  |  |  |  |  |  | W |  |  |  |  |  |  |  |  |
| ref. TYPE VERIFICATIONS AND TYPE TESTS, General purpose connection and junction boxes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Purpose: To ensure that values determined per CONSTRUCTION  ALL APPARATUS, Limiting temperature, are not exceeded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Refer to CONSTRUCTION  ALL APPARATUS, Terminals for external connections |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Refer to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Terminals: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Enclosure or compartment |  |  |  |  |  |  |  |  | Terminal |  |  |  |  |  |  |  |  |
|  | Maximum internal linear dimension L (cm) |  |  | Circuit/terminal identification |  |  |  |  |  | number of terminals | Type | Size conductor cross-sectional area (cm2) | Resistance R terminal + conductor length (L) at 20 C () |  | Power I2R per terminal (W) | Power total for number of terminals (W) |  |  |
|  |  |  |  |  |  |  |  |  | Rated current I (A) |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Ref. No |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sum of dissipated power values (W) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 30 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 13/16 |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  | YES | NO |  |  | ENCL. |  |  |  |  |
| 5.8 |  |  |  | Resistance heating devices and resistance heating units |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating devices and resistance heating units Notes: 1. Not applicable to induction heating, skin effect heating, dielectric heating or any other heating system which involves passing current through a liquid, an enclosure or pipework. 2. Clause 4.6 of this standard (ref. CONSTRUCTION  ALL APPARATUS, Windings) does not apply to heating resistors (these are not considered to be windings). 3. The requirements of IEC 60079-0 for plastic materials do not apply to the insulating materials of heating resistors and to the sheaths of heating cables and tapes. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Heating device; type/manufacturer/part no./ratings/certification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - heating resistor; conductive element material: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | positive temperature coefficient |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | characteristics declared by the manufacturer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | - resistance at 20 C, |  |  |  |  |  |  (tolerance, |  |  |  |  |  |  |  | ) |  |  |  |
|  |  |  |  |  |  |  |  | - maximum operating temperature Tp, |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | - cold start current, |  |  |  |  |  | A at |  |  |  |  | C |  |  |  |  |  |  |
|  |  |  |  |  |  |  | self-limiting property; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cold start current  manufacturer's declared value + 10 % after the first 10 s of energization |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (ref. TYPE VERIFICATIONS AND TYPE TESTS, Resistance heating devices and resistance heating units, Test for cold start current) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Provision for protection of the resistance heating device against abnormal earth fault and earth leakage currents: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | intended to be protected in conjunction with an electrical apparatus in which it is incorporated; criteria: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |  |
|  |  | constructed for use with an electrical protective device (leakage or insulation monitoring) per Annex E such that the function of the protective device is assured by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |  |
|  |  | constructed for use with an electrical protective device (leakage or insulation monitoring) per Annex E such that the function of the protective device is assured by an electrically conductive covering layer of |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | , in which case: |  |  |  |  |  |
| the covering is |  |  |  |  |  |  | evenly distributed over the whole of the insulating sheath surface with |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | coverage  70 % of the insulating surface and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| resistance ( |  |  |  |  |  |  |  |  | ) of the conductive covering for the same length of the heating resistor: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | < heating resistor value at 20 C or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  heating resistor value at 20 C (protective device prevents excessive temperature under fault; for verification ref. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| alternatively, resistance of the conductive covering |  |  |  |  |  |  |  |  |  |  |  |  | in the case of a self-limiting heating resistor: |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  value ( |  |  |  |  | ) of one bus conductor |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Electrical insulation ensuring against heating resistor contact with the potentially explosive atmosphere; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 14/16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 31 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 14/16 |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  | YES |  |  | NO | ENCL. |  |  |  |  |  |  |  |
| 5.8 |  |  |  | Resistance heating devices and resistance heating units (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating devices and resistance heating units (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Conductors for connections to resistance heating device (cross-section, |  |  |  |  |  |  |  |  |  |  |  |  |  |  | mm2); details: |  |  |  |  |  |  |  |  |  |
| Required: conductor cross-section  1 mm2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal insulation (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | : |  |
|  |  |  |  |  |  | not considered as excluding access of the potentially explosive atmosphere |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | considered as excluding access of the potentially explosive atmosphere based on: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Note: These considerations are concerned with the determination of temperature class; however, the latter shall not normally be applied. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Means preventing the resistance heating device or unit from exceeding the limiting temperature ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C): |  |  |  |
|  |  | stabilized design, attaining a maximum temperature of |  |  |  |  |  |  |  |  | C under specified conditions of use, i.e. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | refer to forms for IEC 60079-0, Temperature measurement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | ref. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | self-limiting property (see 13), resulting in a maximum temperature of |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |
|  |  |  |  |  |  | refer to ANNEX C, Verification of limiting temperature, Heating device with self-limiting characteristic |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | ref. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | electrical protective system (ref. Protection by a protective system, 15); cut-off temperature, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C: |  |  |
|  |  |  |  |  |  | independent of any control system for regulating functional temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parameters on which temperature of the resistance heating device depends: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Characteristics defined in manufacturer's documentation; ref. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Heat output |  |  |  |  |  | Temperature of surroundings (gas, liquid, workpiece) |  |  |  |  |  | Heat transfer to surroundings |  |  |  |  |  |  |  |  |  |  |  |
| continued on 15/16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 32 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  |  |  | SUPPLEMENTARY  SPECIFIC APPARATUS 15/16 |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  | YES |  | NO |  |  | ENCL. |  |  |  |  |
| 5.8 |  |  |  |  |  |  |  | Resistance heating devices and resistance heating units (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating devices and resistance heating units (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Protection by a protective system; methods: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | sensing temperature of the resistance heating device; accomplished by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |  |
|  |  |  | sensing temperature of the immediate surroundings of the resistance heating device; accomplished by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |  |
|  |  |  | sensing the surrounding temperature; accomplished by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | and by sensing (other parameters) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ; accomplished by: |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |  |
|  |  |  | sensing parameters other than temperature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ; accomplished by: |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | and |  |  |  |
| 2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ; accomplished by: |  |  |  |  |  |
| Note: Examples of parameters other than temperature are level, flow, current, leakage current, power consumption. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Protective system (features): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | system de-energizes resistance heating device/unit ( |  |  |  |  |  |  |  |  |  |  | directly ) ( |  |  |  | indirectly) |  |  |  |  |  |  |
|  |  | - method of re-enabling the resistance heating device/unit: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | system (protective device) must be manually replaced and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | manufacturer's instructions specify replacement parts (in the case of a thermal fuse) |  |  |  |  |  |  |  |  |  |  |
| or |  |  |  |  |  |  |  |  |  | system has to be manually reset after the resistance heating device/unit has returned to its normal operating condition and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | replacement of the system requires the use of a tool |  |  |  |  |  |  |  |  |  |  |
| or |  |  |  |  |  |  |  |  |  | automatic reset, with continuous monitoring of the protective system information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | in the event of sensor failure the heating device is de-energized before the limiting temperature is reached; ref. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | adjustment of the protective device is locked and sealed so as to ensure against alteration in service; method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | system operates under abnormal conditions; ref. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Special conditions for safe use: (e.g. in the case of a resistance heating unit supplied with an incomplete protective system) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - ref. document |  |  |  |  |  |  |  |  |  |  |  |  |  |  | for appropriate instructions |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | marking includes the sign "X" |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Refer to TYPE VERIFICATIONS AND TYPE TESTS, Resistance heating devices and resistance heating units and Routine verification and routine tests, Electric strength test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 33 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  | SUPPLEMENTARY  SPECIFIC APPARATUS 16/16 |  |  | APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  | REQUIREMENTS |  |  | YES | NO | ENCL. |  |
| 5.9 |  | Other electrical apparatus |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |
| Other electrical apparatus |  |  |  |  |  |  |  |  |
| The following supplementary requirements for specific apparatus are considered applicable for purposes indicated: |  |  |  |  |  |  |  |  |
| Requirement |  |  |  | Applied to: (apparatus/part/circuit/component) | Purpose |  |  |  |
|  |  |  | ref. Sheet (No) |  |  |  |  |  |
| Note: See also CONSTRUCTION  ALL APPARATUS. |  |  |  |  |  |  |  |  |

Sheet 34 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | TYPE VERIFICATIONS AND TYPE TESTS 1/10 |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | YES | NO | ENCL. |  |  |  |  |  |
| 6.1 |  |  |  |  | Electric strength |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: The applicable test requirements of IEC 60079-0 are supplemented by tests specific to type of protection 'e' in the forms which follow. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Electric strength |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test to specific standard: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Entire apparatus |  | Part/component |  |  | Specific standard and clause |  |  | Rated voltage UN (V) |  | Test voltage r.m.s. a.c. or d.c. (V) | Applied between: |  |  |  |  |  | Breakdown (NO/YES) |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | period (min) | at operating temperature |  |  |  |
|  | (X) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | (X) |  |  |  |
| Alternatively (where there is no test requirement): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Entire apparatus | Part/component |  |  |  | Test voltage (+5 %, -0 %) |  |  |  |  | Applied between: |  |  |  |  |  | Breakdown (NO/YES) |  |  |
|  |  |  |  |  |  |  | 500 V r.m.s. (supply voltage  90 V peak) | Supply voltage > 90 V peak (greater of:) |  |  | Resistance heating device/unit |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | period (min) Required: 1 min +5 %, -0 % | at operating temperature |  |  |  |
|  |  |  |  |  |  |  |  | 1000 + 2U where U = rated volts (V) |  | 1500 V r.m.s. | 1000 + 2U where U = rated volts (V) |  |  |  |  |  |  |  |  |  |
|  |  | (X) |  |  |  |  | (X) |  |  | (X) |  |  |  |  |  |  | (X) |  |  |  |

Sheet 35 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  | TYPE VERIFICATIONS AND TYPE TESTS 2/10 |  |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  | YES | NO |  | ENCL. |  |  |
| 6.2 |  |  |  |  |  | Rotating electrical machines |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rotating electrical machines |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ratings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | V, |  |  | Hz, |  |  | A (IN), ( |  |  |  |  |  | phase); rated output P, |  |  |  |  | kW/(kVA) |  |
|  |  |  | continuous duty |  |  |  |  |  |  | short-time duty |  |  |  |  |  |  | periodic duty |  |  |  |  |  |  |  |  |
| Determination of starting current ratio IA/IN and time tE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature rise in rated service: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ref. ANNEX B  CAGE MOTORS – METHODS OF TEST AND OF CALCULATION, Temperature rise of stator and rotor windings in rated service |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | refer to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature rise in stalled motor: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ref. ANNEX B  CAGE MOTORS – METHODS OF TEST AND OF CALCULATION, Temperature rise in stalled motors (determined experimentally) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | ref. ANNEX B  CAGE MOTORS – METHODS OF TEST AND OF CALCULATION, Temperature rise in stalled motors (calculated) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Figures derived by calculation (values of temperature rise referring to rated service and stalled condition) due to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | machine rating > 160 kW |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 75 kW < machine rating < 160 kW (the manufacturer and testing station agree to accept calculated figures since neither has adequate test facilities) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Orientation during tests: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | axis horizontal |  |  |  |  |  |  | axis vertical |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (intended operating position(s); |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
|  |  |  | Note: Machines may tested in the horizontal position even if intended for use in positions other than horizontal, provided test conditions are equivalent to service conditions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 36 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | TYPE VERIFICATIONS AND TYPE TESTS 3/10 |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  | YES |  |  |  | NO |  |  | ENCL. |  |  |  |  |  |
| 6.3 |  |  |  | Luminaires designed for mains supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Luminaires designed for mains supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mechanical tests for screwed lampholders: (E10 lamp cap excluded; see also ANNEX A) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Test lamp cap (IEC 60238) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Size |  |  |  | test lamp cap fully inserted | Ref. Table 7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | Insertion torque (N.m) Required: 1.0  0.1 N.m (E14) 1.5  0.1 N.m (E27) 3.0  0.1 N.m (E40) |  |  | Removal torque (N.m) Required minimum: 0.3 N.m (E14) 0.5 N.m (E27) 1.0 N.m (E40) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | measured after rotating test lamp cap 15 |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | E14 | E27 | E40 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | (X) | (X) | (X) |  | (X) |  |  |  |  |  |  |  | (X) |  |  |  |  |  |  |  |  |  |  |  |
| Thermal test for luminaires with tubular fluorescent lamps |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | diode(s) connected in series with lamp(s) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 110 % of rated voltage (rated voltage, |  |  |  |  |  |  |  |  |  |  | V  1.1 = |  |  |  | V): |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Component/surface/part |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Temperature |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Method |  |  |  |  |  |  | (C) |  |  |  |
|  | ambient: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| maximum temperature value, corrected for maximum service ambient ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C), |  |  |  | C |  |  |
| maximum surface temperature per IEC 60079-0, for the temperature class, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C |  |  |
| rated voltage: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Ballast windings (location) |  |  |  |  |  |  |  |  |  |  |  |  | Temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Measured |  |  |  |  |  |  |  |  |  |  | Limiting value (C) |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Method |  |  |  |  |  |  | (C) |  |  |  |  |  |  |  |
|  | ambient |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (refer to CONSTRUCTION  ALL APPARATUS, Limiting temperature) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 37 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  |  | TYPE VERIFICATIONS AND TYPE TESTS 4/10 |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  | YES | NO |  |  | ENCL. |  |  |  |
| 6.4 |  |  |  |  |  |  | Measuring instruments and instrument transformers |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Measuring instruments and instrument transformers |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal and dynamic stresses: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Ref. SUPPLEMENTARY  SPECIFIC APPARATUS, Measuring instruments and instrument transformers, Current transformers and current-carrying parts of measuring instruments: |  |  |  |  |  |  |  |  |  |  |  | Applied to (part) |  |  | evidence of reduced level of security against explosions NO/YES | Temperature |  |  |  |  |
|  | Ith r.m.s. primary current  Ith |  |  |  |  |  |  | Idyn peak primary current  Idyn |  |  |  | Condition No (from Sheet 6/16 of the above reference) |  |  |  |  | Rise, K, + service temperature (C) for service temperature ref. forms for IEC 79-0, Temperature measurement |  | Limiting value (C) ref. CONSTRUCTION  ALL APPARATUS, Limiting temperature |  |  |
|  | Thermal test of current transformer (secondary short-circuited) |  | Thermal test of current-carrying parts |  | Test duration (s)  1 s | Test current (A) |  | Dynamic test of current transformer (secondary short-circuited) | Dynamic test of current-carrying parts | Test duration (s)  0.01 s | Test current I (A) applied for at least one peak |  |  |  |  |  |  |  |  |  |  |
|  | (X) |  | (X) |  |  |  |  | (X) | (X) |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: Where the dynamic test is combined with the thermal test the following are applicable: - first major peak of test current  Idyn and - I is applied for time t such that I2t  (Ith)2 and - 0.5 s < t < 5 s |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Ambient |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Method |  |  | (C) |  |  |
| For limiting values of temperature at Ith refer to CONSTRUCTION  ALL APPARATUS, Limiting temperature. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method(s) of determining temperature rise: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 5/10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 38 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | TYPE VERIFICATIONS AND TYPE TESTS 5/10 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES | NO |  | ENCL. |  |
| 6.4 |  |  |  | Measuring instruments and instrument transformers (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.5 |  |  |  | Transformers other than instrument transformers |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Measuring instruments and instrument transformers (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Interturn overvoltage test of current transformer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | secondary windings open-circuited (or connected to high impedance peak voltage reading instrument) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | sinusoidal current at |  |  |  |  |  | Hz (40 – 60 Hz) applied for 60 s to primary winding, subject to a maximum value of |  |  |  |  |  |  |  |  |  |  |  |
| 1.2  rated primary current ( |  |  |  |  |  |  |  |  |  |  |  | A) = |  |  |  | A |  |  |
| or |  |  |  |  |  |  |  | limited to |  | A on attaining voltage (in secondary) of 4.5 kV peak |  |  |  |  |  |  |  |  |
| Result: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | no breakdown |  |  |  |  |  |  | breakdown |  |  |  |  |  |  |  |  |  |  |
| Transformers other than instrument transformers |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature test conditions: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | specified load forms part of the apparatus |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | specified load does not form part of the apparatus (e.g. remote interconnected device), in which case adverse load conditions including secondary winding short-circuit are considered |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | protective device in circuit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature test data: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to forms for IEC 60079-0, Temperature measurement |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 39 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  |  | TYPE VERIFICATIONS AND TYPE TESTS 6/10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  | NO |  |  | ENCL. |  |  |  |  |  |
| 6.6 |  |  |  |  |  |  | Secondary batteries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.6.1 |  |  |  |  |  |  | Insulation resistance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.6.2 |  |  |  |  |  |  | Shock test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Secondary batteries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insulation resistance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test conditions: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | - ohmmeter measuring voltage, |  |  |  |  |  |  |  |  |  |  |  | V  100 V required |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | connections between battery and external circuits ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | and battery container) disconnected |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | cells filled with electrolyte up to the maximum permissible level |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | - insulation resistance measured between live parts and battery container, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | M  1 M required |  |  |  |  |  |  |  |
| Shock test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | applicable (batteries are subject to mechanical shocks in normal service) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | not applicable (marking includes the sign "X" indicating special conditions of safe use) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Shock test: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Test conditions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Test procedure |  |  |  |  |  |  |  |  |  |  | Acceptance criteria |  |  |  |  |
|  | Samples new fully-charged cells complete with intercell connectors, installed in a suitable container |  |  |  |  |  |  | Sample mounting on shock machine per Cl. 4.3 of IEC 68-2-27 ref. IEC 68-2-47 also |  |  |  |  | Shock machine per references to IEC 68-2-27 (below) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |
|  | Sample No ( multiple samples representing a range of capacities) |  |  |  | Cell capacity rating and configuration each test sample shall comprise at least 2  2 cells |  |  | in normal operating attitude | by its normal means of attachment | fixing method |  |  | half-sine (trapezoidal) pulse per Fig. 3 | velocity change tolerances per Cl. 4.1.2 |  | transverse motion tolerance per Cl. 4.1.3 | measuring system characteristics per Cl. 4.2 | peak acceleration value of 5 gn per Table 1 in Cl. 5 |  | Capacity (initial) |  | 15 independent shocks applied |  |  |  |  |  |  | Capacity (after recharging) |  | no abrupt change in voltage | no visible damage/deformation | no reduction in capacity > 5 % |  |  |
|  |  |  |  |  |  |  |  |  |  | directly to machine mounting surface |  | by means of a rigid fixture (alternative) |  |  |  |  |  |  |  |  |  | constant 5 h discharge current |  |  | 3, successive; vertically upwards direction | 3, successive, in each direction along two perpendicular axes in the horizontal plane |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | axes in the horizontal plane chosen so as to reveal possible weaknesses |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | (X) | (X) | (X) |  | (X) | (X) | (X) |  | (X) | (X) | (X) |  | (Ah) |  | (A) |  |  | (X) | (X) |  | (X) | (Ah) |  | (X) | (X) | (X) |  |  |

Sheet 40 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  | TYPE VERIFICATIONS AND TYPE TESTS 7/10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  |  | NO |  |  | ENCL. |  |  |  |  |  |
| 6.6.3 |  |  | Test for adequate ventilation of battery container |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test for adequate ventilation of battery container |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| *Volume of hydrogen required to be released within battery container: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | pure hydrogen; flow rate = number of cells ( |  |  |  |  |  |  |  |  |  |  | )  capacity ( |  |  |  |  |  |  | Ah)  5  106 = |  |  |  |  |  |  |  |  |  | m3/h |  |
|  | impure hydrogen (purity, |  |  |  |  |  |  | %), compensated by flow rate increase to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | m3/h |  |  |  |  |  |
| Method 1: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | battery container fitted with closed boxes (having filler and vent plugs of identical form, number and location as for cells) in place of cells, located so as to retain normally existing natural ventilation between cells |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | constant *flow of hydrogen fed (equally distributed) to filler and vent plugs, into the space above the boxes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method 2: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | battery container equipped with a battery made up of cells of number, type and capacity as intended in service |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | overcharging current applied to produce a constant flow of hydrogen in accordance with the formula, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Overcharging current = |  |  |  |  |  |  |  | hydrogen (m3/h; *as determined above) |  |  |  |  |  |  |  |  |  |  |  |  |  | = |  |  |  |  | A |  |  |
|  |  |  |  |  |  |  |  |  | number of cells ( |  |  |  |  |  | )  0.44  103 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Determination of maximum hydrogen concentration within the battery container: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Method 1 | Method 2 | Measurement of hydrogen concentration last listed value of % H2  105% of the mean of 4 consecutive measurements |  |  |  |  |  |  | Temperature (C) values shall not differ by more than 4 K (15 C < value < 25 C) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | No | Time interval (min.) |  | % H2 |  | Increase from mean |  | Ambient |  |  |  | Battery container |  |  |  | Cells (Method 2) or boxes simulating cells (Method 1) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  5% | > 5% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | (X) | (X) |  |  |  |  |  | (X) | (X) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 1ST trial: |  |  |  |  |  |  |  |  |  | ---- | ---- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | ---- | ---- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | ---- | ---- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 2ND trial: |  |  |  |  |  |  |  |  |  | ---- | ---- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | ---- | ---- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | ---- | ---- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Maximum of listed (last) values: not to exceed 2% |  |  |  |  |  |  |  |  |  | method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Notes: 1. Tests conducted at the barometric pressure of the testing station, in a draught-free area. 2. Measurements shall be made so as to ensure that % H2 is concentration within battery container (not as released from filler/vent plugs). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 41 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  | TYPE VERIFICATIONS AND TYPE TESTS 8/10 |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  | YES | NO |  |  | ENCL. |  |  |  |  |
| 6.7 |  |  |  |  |  | General purpose connection and junction boxes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General purpose connection and junction boxes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Determination of "worst case" terminal (i.e. where more than one type/size of terminal is used): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Ref. SUPPLEMENTARY  SPECIFIC APPARATUS, General purpose connection and junction boxes, Terminals: |  |  |  |  | Temperature test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Duration (min.) sufficient to attain steady state |  |  | Temperature |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Test current (A) i.e. rated current of terminal |  |  | Length of wire connected to terminal (cm) maximum size of conductor of length corresponding to dimension L |  |  |  |  | Rise K |  | Method |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | applied to terminal (Ref. No) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Ambient (C) |  | Method |  |  |  |  |  |  |  |  |  |
| Maximum permissible dissipated power based on temperature of hottest part with "worst case" terminals fitted: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Ref. SUPPLEMENTARY  SPECIFIC APPARATUS, General purpose connection and junction boxes, Terminals: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Temperature of hottest part |  |  |  |  |  |  |  |  |  |  |
|  | Test current (A) i.e. rated current of terminal applied to terminals wired in series |  | Test terminals |  |  |  |  |  |  |  |  | Wiring of terminals |  |  | Power I2R per terminal (W) |  | Location |  |  |  | (C) |  |  | Method |  |  |  |
|  |  |  | applied to terminal per Ref. No | number of terminals | number of terminals based on: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | maximum number of terminals accommodated by enclosure |  | maximum number of terminals provided in service |  | (other reason) |  |  | Length of wiring per terminal (cm) maximum size of conductor of length corresponding to dimension L |  | terminals series-connected with conductors in groups of six |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | (X) |  | (X) |  |  |  |  |  |  | (X) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Maximum total dissipated power (W): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ambient: |  |  |  |  |  |  |  |  |  |  |
|  | Limiting value; ref. CONSTRUCTION  ALL APPARATUS, Limiting temperature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |

Sheet 42 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | TYPE VERIFICATIONS AND TYPE TESTS 9/10 |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  | YES |  |  | NO |  |  | ENCL. |  |  |  |  |
| 6.8 |  |  |  | Resistance heating devices and resistance heating units |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating devices and resistance heating units (tests conducted on sample or prototype resistance heating device) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ref. SUPPLEMENTARY  SPECIFIC APPARATUS, 13/16, Resistance heating devices and resistance heating units |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Heating device: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | heating resistor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | heating cable; sample length, |  |  |  |  | m  3 m ( |  |  |  | including constructional discontinuities: |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
|  |  |  |  |  | possible installed length of cable > 75 m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | heating tape; sample length, |  |  |  |  | m  3 m ( |  |  |  | including constructional discontinuities: |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
|  |  |  |  |  | possible installed length of tape > 75 m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (other) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verification of electrical insulation: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Relevant part of sample |  |  |  |  |  |  |  | Temperature (C) 10 <C < 25 (throughout all steps) |  |  | Insulation integrity test |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Voltage applied for 1 min. (sample immersed in tap water) |  |  |  |  |  |  |  |  | Insulation resistance measured with 500 V d.c. (nominal) source voltage (M) Required:  20 M ( 500 M for a 3 m sample in case of possible installed length of cable or tape exceeding 75 m) |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 500 + 2 U U = rated voltage of apparatus (V) |  | Single heating conductor |  |  | Multiple heating conductors (connections may be broken) |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | immersed 30 min. in tap water |  |  |  |  |  | between the conductor and the conductive covering | between the conductor and the water (no conductive covering) |  | between each pair of conductors | between each conductor and the conductive covering |  | between each conductor and the water (no conductive covering) |  |  |  |
|  |  |  |  |  |  |  |  | (X) |  |  |  |  |  | (X) | (X) |  | (X) | (X) |  | (X) |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- | ---- |  |  | ---- |  | ---- |  |  |  |
| continued on 10/10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 43 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  | TYPE VERIFICATIONS AND TYPE TESTS 10/10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  |  |  | NO |  |  | ENCL. |  |  |  |  |  |  |
| 6.8 |  |  | Resistance heating devices and resistance heating units (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating devices and resistance heating units (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insulation integrity test (applicable to tests below): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Relevant part of sample |  |  |  |  |  |  |  |  |  |  | sample, conditioned per thermal stability evaluation (below) |  | sample (cable or tape), subjected to test for resistance to impact (below) |  |  |  |  | Temperature (C) 10 <C < 25 (throughout all steps) |  |  |  | Voltage applied for 1 min. (sample immersed in tap water) |  |  |  |  |  |  |  |  |  |  |  |  | Insulation resistance measured with 500 V d.c. (nominal) source voltage (M) Required:  20 M ( 500 M for a 3 m sample in case of possible installed length of cable or tape exceeding 75 m) |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 500 + 2 U U = rated voltage of apparatus (V) |  |  | Single heating conductor |  |  |  |  | Multiple heating conductors (connections may be broken) |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | between the conductor and the conductive covering |  | between the conductor and the water (no conductive covering) |  |  | between each pair of conductors | between each conductor and the conductive covering |  | between each conductor and the water (no conductive covering) |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | (X) |  | (X) |  |  |  |  |  |  |  |  |  |  |  | (X) |  | (X) |  |  | (X) | (X) |  | (X) |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  | ---- |  |  |  | ---- |  | ---- |  |  |  |  |  |
|  | impacted area of cable or tape (Sample 1) |  |  |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  | ---- |  |  |  | ---- |  | ---- |  |  |  |  |  |
|  | impacted area of cable or tape (Sample 2) |  |  |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  | ---- |  |  |  | ---- |  | ---- |  |  |  |  |  |
| Thermal stability of insulating materials: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | sample stored in air at (Tp + 20) C ( |  |  |  |  |  |  |  |  |  |  |  |  |  | C) for |  |  |  |  |  |  | weeks  4 weeks at operating temp. + 20 C ( 80 C) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | sample, in turn, stored in air at |  |  |  |  |  |  |  |  |  |  | C for |  |  |  |  |  |  |  |  | h 30 < C < 25 for  24 h |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | sample subjected to insulation integrity test (above) to verify compliance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test for resistance to impact of resistance heating device: (conducted on two new samples) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | not applied (resistance heating device/unit is protected by an enclosure complying with the Test for resistance to impact of IEC 60079-0) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ref. forms for IEC 60079-0, Test for resistance to impact |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | 7 J |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 J |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - impact head (cable/tape): |  |  |  |  |  | 25 mm dia. steel cylinder (adequate length to cover total width of cable or tape), oriented at 90 to axis of sample |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | samples subjected to insulation integrity test (above) to verify compliance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test for cold start current: (conducted on 3 samples of the resistance heating device attached to thermal mass/heat sink in cold chamber) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | - stabilized cold chamber temperature, |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C manufacturer's declared cold start temperature  2 C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | - operating voltage ( |  |  |  |  |  | V) applied; maximum current after 10 s through first minute of energization: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Sample 1, |  |  |  |  |  |  |  |  |  | A |  |  |  |  | Sample 2, |  |  |  |  |  |  | A |  | Sample 3, |  |  |  |  |  |  |  | A |  |  |
| Tests for specific form of resistance heating device or unit (including verification of limiting temperature): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to ANNEX C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 44 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  |  |  | ROUTINE VERIFICATION AND ROUTINE TESTS 1/1 |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  | YES | NO | ENCL. |  |  |  |
| 7.1 |  |  |  |  |  |  | Electric strength test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2 |  |  |  |  |  |  | Electric strength test (batteries) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | The manufacturer agrees to perform routine tests per the procedures outlined below: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: The following supplement the requirements of IEC 60079-0. See also forms for IEC 60079-0. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Electric strength test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Test to specific standard: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Apparatus (or part/component) |  |  |  |  |  |  |  |  | Specific standard and clause |  |  |  | Test voltage r.m.s. a.c. or d.c. (V) |  | Applied between: |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | period (min) |  |  |
|  |  |  |  |  | Alternatively (where there is no test requirement): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Apparatus (or part/component) |  |  |  |  |  |  |  |  | Test voltage (+5 %, -0 %) |  |  |  |  |  | Applied between: for 1 min +5 %, -0 % |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 500 V r.m.s. (supply voltage  90 V peak) |  | Supply voltage > 90 V peak (greater of:) |  | Resistance heating device/unit |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 1000 + 2U where U = rated volts (V) | 1500 V r.m.s. | 1000 + 2U where U = rated volts (V) |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | (X) |  |  | (X) |  |  |  |  |  |  |  |  |  |
| Electric strength test (batteries) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insulation resistance: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | ohmmeter measuring voltage, |  |  |  |  |  |  | V  100 V required |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | connections between battery and external circuits ( |  |  |  |  |  |  |  |  |  | and battery container) disconnected |  |  |  |  |  |  |  |  |
|  |  |  |  |  | cells filled with electrolyte up to the maximum permissible level |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | measured insulation resistance, |  |  |  |  |  |  |  |  | M  1 M required |  |  |  |  |  |  |  |  |  |  |  |

Sheet 45 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| IEC 60079-7 |  |  |  |  |  |  | MARKING 1/2 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES | NO | ENCL. |  |
| 8 |  |  |  |  |  |  | Marking |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: For major marking content refer to forms for IEC 60079-0, Marking. These sheets cover specific marking for the type of protection. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Marking |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | rated voltage |  |  |  |  |  |  |  |  | rated current |  |  |  |  |  |  |  |  |  |  |
| Rotating electrical machine/a.c. magnet (overload protection): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | starting current ratio IA/IN |  |  |  |  |  |  |  |  |  |  |  |  |  | time tE (s) |  |  |  |  |  |
|  | associated (specific) protective device: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Measuring instrument/instrument transformer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | rated short-time thermal current Ith |  |  |  |  |  |  |  |  |  |  |  |  |  | rated dynamic current Idyn |  |  |  |  |  |
| Luminaire; technical data of lamp(s) to be used (e.g.): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (rating) |  |  |  |  |  |  |  |  | (dimensions) |  |  |  |  |  |  |  |  |  |  |
| Note: A dispensation for a lamp (having surface temperature + 50 K  lowest temperature of ignition, inside a luminaire, of the explosive atmosphere(s) for which the luminaire is intended, where interior surface temperature exceeds the maximum surface value prescribed by IEC 60079-0), requires the specific gas atmosphere(s) to be indicated in the certificate. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General purpose terminal or junction box: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | permissible maximum dissipated power |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Restrictions in use (e.g.): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (use in clean environments only) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Characteristics of special protective devices (e.g.): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (temperature control) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (arduous starting conditions; Annex B, D) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (special supply conditions; converters) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Secondary batteries: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | type of cells |  |  |  |  |  |  |  |  | number of cells |  |  |  |  | nominal voltage |  |  |  |  |  |
|  | rated capacity with corresponding duration of discharge |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | warning label "SEPARATE ONLY IN A NON-HAZARDOUS AREA" (plugs/sockets separable only with the use of a tool) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | warning plate "DO NOT CHARGE IN A HAZARDOUS AREA" on battery container (where no safety measures are incorporated for charging in the hazardous area) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | information and instructions for charging/use/maintenance/safe operation (for display in the battery charging station) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating devices and resistance heating units: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | operating temperature Tp |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: The manufacturer should state the minimum permissible bending radius and temperature at which a flexible heating device may be formed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reduced degree of protection by enclosure: |  |  |  |  |  |  |  |  |  |  | E.g. Rotating electrical machine for use only in clean environments or enclosure with degree of protection reduced by drain holes or ventilation openings. |  |  |  |  |  |  |  |  |  |
|  | IP |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 2/2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 46 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | MARKING 2/2 | APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS | YES | NO | ENCL. |  |
| 8 |  |  |  |  | Marking (continued) |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |
| Marking (continued) |  |  |  |  |  |  |  |  |  |
| Sign "X", indicating special conditions noted in the certificate in accordance with the following: |  |  |  |  |  |  |  |  |  |
|  | degree of protection provided by enclosure reduced by drain holes or ventilation openings |  |  |  |  |  |  |  |  |
|  | enclosed ventilated rotating electrical machine for use only with pipe connections for cooling air inlet/outlet |  |  |  |  |  |  |  |  |
|  | rotating electrical machine for use only in clean environments |  |  |  |  |  |  |  |  |
|  | resistance heating unit supplied with an incomplete protective system (as an example, for features of protective system) |  |  |  |  |  |  |  |  |
|  | secondary battery not to be subjected to mechanical shocks in normal service |  |  |  |  |  |  |  |  |

Sheet 47 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | ANNEX A  LAMPHOLDERS AND LAMP CAPS FOR LUMINAIRES DESIGNED FOR MAINS SUPPLY 1/2 |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | YES |  | NO |  | ENCL. |  |  |  |  |  |
| A.1 |  |  |  |  | Test for non-transmission of an internal ignition |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A.2 |  |  |  |  | Screw lampholders |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test for non-transmission of an internal ignition |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lampholder with appropriate lamp cap fitted: (ref. SUPPLEMENTARY  SPECIFIC APPARATUS, 3/16, Luminaires designed for mains supply) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | placed in test chamber (volume |  |  |  |  |  |  |  |  |  | ) |  |  |  |  |  |  |  |  |  |  |
|  |  | same test mixture throughout |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | volume ratio of test chamber to enclosed volume of lampholder  5 to 1 for Group II test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Test No |  | Ignition source/location |  |  |  |  | Notes (test set-up, method, etc.) |  |  | Flame transmission (NO/YES) |  | Method |  |  | Test mixture (IEC 60079-1, Table IV) |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Group I; IEC 60079-1, Cl. 14.2.1.1 (tested in normal condition) | Group II; IEC 60079-1, Cl. 14.2.2.2 (tested in normal condition) |  | Group I; 12.5  0.5 % methane-hydrogen (58/42  1 %) |  | Group IIC; 27  1.0 % hydrogen | Group IIC; 7.5  1 % acetylene | C |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Test mixture pressure (bar) |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | (X) | (X) |  | (X) |  | (X) | (X) |  |  |  |
| Screw lampholders |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | subjected to test for non-transmission of an internal ignition (as above) or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | lampholder fitted with quick-acting switch with an enclosure meeting construction test requirements for non-transmission of an internal ignition: (e.g. a component Ex d switch) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | - details, including manufacturer/part no./rating; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | certified ( |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
| or |  |  |  |  |  |  | refer to forms for IEC 60079-1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 2/2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 48 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | ANNEX A  LAMPHOLDERS AND LAMP CAPS FOR LUMINAIRES DESIGNED FOR MAINS SUPPLY 2/2 |  |  |  |  |  |  | APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  | YES | NO |  | ENCL. |  |
| A.2 |  |  |  | Screw lampholders (continued) |  |  |  |  |  |  |  |  |  |  |  |
| A.3 |  |  |  | Lampholders for tubular fluorescent lamps |  |  |  |  |  |  |  |  |  |  |  |
| A.4 |  |  |  | Other lampholders |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Screw lampholders (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insertion and removal torques: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ref. TYPE VERIFICATIONS AND TYPE TESTS, Luminaires designed for mains supply, Mechanical tests for screwed lampholders |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Creepage distances and clearances: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ref. CONSTRUCTION  ALL APPARATUS, 3/8, Clearances and 4/8, Creepage distances: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - compliance with minimum requirements of Table A.1; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | for U  60 V, creepage distance and clearance  2 mm |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | for 60 < U  250 V, creepage distance and clearance  3 mm |  |  |  |  |  |  |  |  |  |
|  | Grade a insulation (Table 2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Lampholders for tubular fluorescent lamps (ref. SUPPLEMENTARY  SPECIFIC APPARATUS, 3/16, Luminaires designed for mains supply) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Compliance with dimensional requirements of data sheet Fa6 (IEC 61-2): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Dimension (mm) |  |  |  |  | Reference document (if provided) |  |  |  |  |  |
|  |  |  |  |  | (data sheet Fa6; IEC 61-2) |  |  |  | Actual |  |  |  |  |  |  |
|  |  |  |  |  | Code |  | Min. | Max. |  |  |  |  |  |  |  |
|  |  |  |  |  | D |  |  | d + 0.1 |  |  |  |  |  |  |  |
|  |  |  |  |  | E |  | 6.03 | 6.08 |  |  |  |  |  |  |  |
|  |  |  |  |  | G |  | 14.5 |  |  |  |  |  |  |  |  |
|  |  |  |  |  | H |  | 1.0 |  |  |  |  |  |  |  |  |
|  |  |  |  |  | J |  | 5.0 |  |  |  |  |  |  |  |  |
| Other lampholders |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Length of path through joint between lampholder and cap/pin (of lamp), at the moment of contact separation: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | measured, |  |  |  | mm  10 mm required |  |  |  |  |  |  |  |  |  |  |

Sheet 49 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  | ANNEX B  CAGE MOTORS – METHODS OF TEST AND OF CALCULATION 1/3 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES |  | NO |  |  |  |  | ENCL. |  |  |  |  |  |  |
| B.1 |  |  | Temperature rise of stator and rotor windings in rated service |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B.2 |  |  | Temperature rise in stalled motors (determined experimentally) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature rise of stator and rotor windings in rated service (ref. IEC 60034-1 and IEC 60079-7,Table B.1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Thermal test |  |  |  | Winding temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Operating condition (according to rated duty) |  |  | Duration (h) | Winding |  |  | Cold resistance, R1 at ambient () |  |  | At end of thermal test |  |  |  |  |  |  |  |  |  |  |  | Limiting value (C) (ref. CONSTRUCTION  ALL APPARATUS, Limiting temperature) |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Initial resistance, R2 () | Measured within: |  |  |  |  |  |  | Rise, K |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Time after switch-off (s) |  | short stopping time (Note 1) |  |  | extended stopping time (Note 2) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | (X) |  |  | (X) |  |  |  |  |  |  |  |  |  |
|  | Notes: 1. Short stopping time = time after switch-off per Table B.1 (a value obtained within this interval is taken as the maximum temperature rise). 2. Extended stopping time  2  time after switch-off per Table B.1 where a resistance reading is not possible within the prescribed time interval (in which case additional resistance readings are plotted and extrapolated to the time interval to determine the value shown). |  |  |  |  |  |  |  |  |  |  |  |  | Ambient |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Method |  |  |  |  |  |  |  |  | (C) |  |  |  |
| Temperature rise in stalled motors (determined experimentally) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Stalled motor initially at ambient ( |  |  |  |  |  |  | C) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test voltage (UT) at rated frequency ( |  |  |  |  |  |  | Hz): |  |  | rated voltage (UN) |  |  |  |  |  |  |  | < rated, |  |  |  |  |  | V |  |  |
| Stator current ( UN /UT) measured 5 s after switching on, IA , |  |  |  |  |  |  |  |  |  |  |  |  | A |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature rises in rotor cage (bars and rings) and of stator winding: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Part/location |  |  |  |  |  |  |  | Method |  |  |  |  |  |  |  | Period monitored, t (s) |  |  |  | Rise () |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Stator – average  (rise of resistance) | Rotor cage |  |  |  |  |  |  |  |  |  |  | measured  (UN /UT)2 saturation considered |  | K |  |  |  |
|  |  |  |  |  |  |  |  |  |  | temperature rises shall be measured by thermocouples (and measuring instruments having time constants that are small compared with /t) or by temperature detectors or other suitable means as noted |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | (X) |  |  |  |  |  |  |  |  |  |  |  | (X) |  |  |  |  |  |
| Note: The highest of the temperatures obtained in the rotor cage is to be considered in the determination of time tE. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 50 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | ANNEX B  CAGE MOTORS – METHODS OF TEST AND OF CALCULATION 2/3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  | NO |  |  | ENCL. |  |  |  |  |
| B.3 |  |  |  |  | Temperature rise in stalled motors (calculated) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B.4 |  |  |  |  | Determination of time tE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature rise in stalled motors (calculated) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rotor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Calculation of temperature of short-circuited rotor; temperature rise calculated from the joule heating effect: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: Considerations include heat generated in bars/rings, thermal capacity of cage, influence of skin effect on heat distribution in the bars, allowance for heat transfer to the iron. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Stator windings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Starting current density, j, |  |  |  |  |  |  |  |  |  |  |  | A/mm2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Coefficient, a, in K/( A/mm2)2 s: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | copper, 0.0065 |  |  |  |  |  | other material ( |  |  |  |  |  |  |  |  |  |  |  |  | ), |  |  |  |  |  |  |  |  |
| Rate of temperature rise with time: |  |  |  |  |  |  |  |  |  |  | = a  j 2  0.85 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | t |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | = ( |  |  |  |  |  | )  ( |  |  |  | )2  | 0.85 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | = |  |  |  |  |  | K/s |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Determination of time tE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Rotor (hottest part) |  | Stator | Ref. Figure 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | OC |  |  |  | OA |  |  | AB |  |  | BC = OC – (OA + AB) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Limiting temperature (C) |  |  |  | Maximum ambient temperature (e.g. 40 C) (C) |  |  | Temperature rise, K, in rated service |  |  | Difference, K |  | t(2) in s |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Time, tE, for excursion () from service temperature to limiting value (s) |  |  |  |  |  |  |  |  |  |
| (ref. CONSTRUCTION  ALL APPARATUS, Limiting temperature) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Time tE for the motor for the appropriate temperature class (smaller value above): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | s |  |  |  |

Sheet 51 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | ANNEX B  CAGE MOTORS – METHODS OF TEST AND OF CALCULATION 3/3 | APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS | YES | NO | ENCL. |  |
| B.5 |  |  |  |  | Motors designed for arduous starting conditions or provided with special protective devices |  |  |  |  |
| B.6 |  |  |  |  | Motors forming units with converters |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |
| Motors designed for arduous starting conditions or provided with special protective devices |  |  |  |  |  |  |  |  |  |
| Motor designed for arduous starting conditions (see Annex D, Clause D.3): |  |  |  |  |  |  |  |  |  |
|  | associated protective device; reference document(s) and/or details of protective device: |  |  |  |  |  |  |  |  |
| Motor provided with special protective device(s): |  |  |  |  |  |  |  |  |  |
|  | ref. SUPPLEMENTARY  SPECIFIC APPARATUS, 2/16, Machines with cage rotors |  |  |  |  |  |  |  |  |
|  | reference document(s) and/or details of protective device(s): |  |  |  |  |  |  |  |  |
| Test documentation verifying compliance with maximum permissible temperature: |  |  |  |  |  |  |  |  |  |
|  | refer to: |  |  |  |  |  |  |  |  |
| Motors forming units with converters |  |  |  |  |  |  |  |  |  |
|  | ref. SUPPLEMENTARY  SPECIFIC APPARATUS, 2/16, Machines with cage rotors |  |  |  |  |  |  |  |  |
|  | ref. |  |  |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |  |  |  |

Sheet 52 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | ANNEX C  TYPE TESTS FOR SPECIFIC FORMS OF RESISTANCE HEATING DEVICES OR RESISTANCE HEATING UNITS 1/4 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES |  |  |  | NO |  |  |  | ENCL. |  |  |  |  |
| C.1 |  |  |  | Resistance heating devices subjected to mechanical stresses |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating devices subjected to mechanical stresses |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Flexible resistance heating device not protected by an enclosure complying with IEC 60079-0, Test for resistance to impact: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cable |  |  |  | tape |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (such devices are subject to crushing and low temperature bend tests below) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insulation integrity test (applicable to tests below): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Relevant part of sample |  |  |  |  |  | sample, subjected to crushing | sample, subjected to low temperature bending | Temperature (C) 10 <C < 25 (throughout all steps) |  |  |  | Voltage applied for 1 min. (sample immersed in tap water) |  |  |  |  |  |  |  |  |  |  | Insulation resistance measured with 500 V d.c. (nominal) source voltage (M) Required:  20 M ( 500 M for a 3 m sample in case of possible installed length of cable or tape exceeding 75 m) |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 500 + 2 U U = rated voltage of apparatus (V) |  | Single heating conductor |  |  |  | Multiple heating conductors (connections may be broken) |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | between the conductor and the conductive covering |  | between the conductor and the water (no conductive covering) |  | between each pair of conductors | between each conductor and the conductive covering |  |  | between each conductor and the water (no conductive covering) |  |  |  |
|  |  |  |  |  |  |  | (X) | (X) |  |  |  |  |  |  | (X) |  | (X) |  | (X) | (X) |  |  | (X) |  |  |  |
|  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  | ---- |  |  | ---- |  |  | ---- |  |  |  |
|  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- |  | ---- |  |  | ---- |  |  | ---- |  |  |  |
| Crushing test: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | sample placed on rigid flat steel support |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | crushing force of 1500 N applied for 30 s (without shock) by means of 6 mm diameter steel rod having hemispherical ends and a total length of 25 mm with |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | rod laid flat on sample |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| or |  |  |  |  |  | rod placed across sample (cable or tape) at right-angles) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | sample subjected to insulation integrity test (above) to verify compliance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Low temperature bend test: (test apparatus per Figure C.1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | test apparatus, with sample in position, maintained for 4 h at a temperature of |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | 10 C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| or |  |  |  |  |  | lowest temperature declared by manufacturer ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) 3 C |  |  |  |  |  |
|  |  | immediately following conditioning period, sample bent through 90 around one mandrel, then through 180 in the opposite direction over the second mandrel and then straightened to its original position with |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | bending cycle carried out twice (one cycle in about 5 s) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | sample subjected to insulation integrity test (above) to verify compliance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 53 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  | ANNEX C  TYPE TESTS FOR SPECIFIC FORMS OF RESISTANCE HEATING DEVICES OR RESISTANCE HEATING UNITS 2/4 |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  | YES |  |  |  | NO |  |  | ENCL. |  |  |  |  |
| C.2 |  |  |  | Resistance heating devices or units intended for immersion |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C.3 |  |  |  | Resistance heating devices or units having hygroscopic insulating material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insulation integrity test (applicable to tests below): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Relevant part of sample |  |  |  | sample, subjected to immersion (sample immersed in tap water) | sample, subjected to (80  2) C at 90 % r.h. | Temperature (C) 10 <C < 25 (throughout all steps) | Voltage applied for 1 min. |  |  |  |  |  |  |  |  |  | Insulation resistance measured with 500 V d.c. (nominal) source voltage (M) Required:  20 M ( 500 M for a 3 m sample in case of possible installed length of cable or tape exceeding 75 m) |  |  |
|  |  |  |  |  |  |  |  | 500 + 2 U U = rated voltage of apparatus (V) |  |  | Single heating conductor |  |  | Multiple heating conductors (connections may be broken) |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | between the conductor and the conductive covering | between the conductor and the water (no conductive covering) |  | between each pair of conductors | between each conductor and the conductive covering |  | between each conductor and the water (no conductive covering) |  |  |  |
|  |  |  |  |  | (X) | (X) |  |  |  |  | (X) | (X) |  | (X) | (X) |  | (X) |  |  |  |
|  |  |  |  |  |  | ---- |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | ---- | ---- |  |  | ---- |  | ---- |  |  |  |
|  |  |  |  |  | ---- |  |  |  |  |  |  |  |  | ---- |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | ---- | ---- |  |  | ---- |  | ---- |  |  |  |
| Resistance heating devices or units intended for immersion |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | sample (or part of sample intended for immersion) immersed 14 days under 50 mm (+5 mm, 0 mm) of tap water |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | sample subjected to insulation integrity test (above) to verify compliance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: Not intended to verify suitability for immersion in liquids other than water at pressure  500 Pa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating devices or units having hygroscopic insulating material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Parts which ensure vapour tightness ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ): |  |
|  |  | subjected (installed on sample device/unit) to (80  2) C for 4 weeks at |  |  |  |  |  |  |  |  |  |  | % r.h.  90 % required |  |  |  |  |  |  |  |
|  |  | sample (after being wiped dry) subjected to insulation integrity test (above) to verify compliance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (no water immersion during insulation integrity test) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | process/materials to complete the sealing of the resistance heating device or unit are specified in (document): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 54 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | ANNEX C  TYPE TESTS FOR SPECIFIC FORMS OF RESISTANCE HEATING DEVICES OR RESISTANCE HEATING UNITS 3/4 |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | YES | NO |  | ENCL. |  |  |  |  |
| C.4 |  |  |  |  | Verification of limiting temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verification of limiting temperature ref. SUPPLEMENTARY  SPECIFIC APPARATUS, 13/16, 14/16, 15/16, Resistance heating devices and resistance heating units ref. CONSTRUCTION  ALL APPARATUS, Limiting temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Means to prevent the resistance heating device or unit from exceeding the limiting temperature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | resistance heating unit protected by a protective system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | resistance heating unit of stabilized design |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | heating device with self-limiting characteristic |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating unit protected by a protective system Maximum temperature permitted by the protective system: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Conditions applied to the apparatus power output corresponding to 10 % over-voltage with any declared minus tolerance on ohmic resistance |  |  |  |  |  | Protective system |  |  |  |  | Temperature |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | system not included in test |  | system sensing temperature (Note 2) | Note 1 |  | Location |  |  | Method |  |  | C |  |  |
|  |  |  |  |  |  |  | operating conditions not simulated (heating unit regarded as Ex component) | operating conditions simulated |  | system sensing temperature and at least one other parameter (Note 2) | system sensing parameter(s) other than temperature |  |  |  |  |  |  |  |  |  |
|  | Input voltage (V) |  |  | Heating device current (A) |  | Power output (W) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | (X) | (X) | (X) | (X) | (X) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | ambient |  |  |  |  |  |  |  |  |
|  | Details of conditions applied to the protective system or of simulation of operating conditions: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Test duration |  |  |  |
|  | Notes: 1. The most adverse conditions permitted by the devices sensing parameters other than temperature shall be considered. 2. Any additional regulating devices rendered inoperable and thermal inertia considered. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 4/4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 55 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| ###### IEC 60079-7 |  |  |  |  | ANNEX C  TYPE TESTS FOR SPECIFIC FORMS OF RESISTANCE HEATING DEVICES OR RESISTANCE HEATING UNITS 4/4 |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  | YES | NO |  |  | ENCL. |  |  |  |  |  |
| C.4 |  |  |  |  | Verification of limiting temperature (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verification of limiting temperature (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistance heating unit of stabilized design Maximum temperature permitted by the design: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Conditions applied to the apparatus power output corresponding to 10 % over-voltage with any declared minus tolerance on ohmic resistance |  |  |  |  |  |  | Temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Location |  |  |  |  |  | Method |  |  |  |  | C |  |  |
|  | Input voltage (V) |  |  | Heating device current (A) |  | Power output (W) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | ambient |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Details of conditions applied: (worst installation conditions specified by the manufacturer and recognized as such by testing authority) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (e.g. zero fluid flow or empty pipe or vessel) |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Test duration |  |  |  |  |
|  | (X) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | simulated operating conditions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Heating device with self-limiting characteristic (cable, tape or other type of resistance heating device) Maximum temperature permitted by the characteristic: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Conditions |  |  |  |  | Sample (placed within a suitable insulating effectively adiabatic close-fitting box) |  |  |  |  |  |  |  |  | Temperature |  |  |  |  |  |  |
|  | Input voltage (V) |  |  | Heating device current (A) |  | Type/size & dimension(s) |  |  | Method of placement |  | Inside dimensions of box |  |  |  | Test duration |  |  | maximum surface value C measured by thermocouple |  |  |  |
|  |  |  |  |  |  | (X) |  |  | (X) |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | cable or tape (3 m < sample < 4 m) |  |  | cable or tape (close-coiled) |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 56 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)

| IEC 60079-7 |  | COMMENTS |  |  |
| --- | --- | --- | --- | --- |
| #### Clause |  |  | Page |  |

Sheet 57 of 57 	(IEC 60079-7, 1990, Amendments 1 & 2)