- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

TITLE: Draft ExTAG Decision Sheet – Temperature rise of the conductor bar for terminals in Level of Protection “eb” according to IEC 60079-7

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

This document, ExTAG/456A/CD Draft ExTAG Decision Sheet – Temperature rise of the conductor bar for terminals in Level of Protection “eb” according to IEC 60079-7, has been prepared by LCIE.

In light of the comments received, circulated in ExTAG/463/CC, this updated version, ExTAG/456A/CD has been prepared for consideration during the ExTAG Washington, USA, Meeting

Changes to the original edition are shown using the tracking tool.

Christine Kane

If there are no comments received the document will be forwarded for publication.

Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

COLLECTION OF IECEx / ExTAG DECISION

| Standard: IEC 60079-7:2015 (Ed. 5.0) | Clause: 4.2.2.2 | Date: 2017-06-28 Originator of proposal: LCIE |
| --- | --- | --- |
| Subject: Temperature rise of the conductor bar for terminals in Level of Protection “eb” according to IEC 60079-7 Status: Draft | Key words: - Terminals - Ex Component | TC/SC involved: MT 60079-7 Draft Decision Sheet: |
| Background: In clause 4.2.2.2 of IEC 60079-7 Edition 5.0, it is specified that the temperature rise of the conductor bar for terminals in Level of Protection “eb” shall not exceed 40 K at a test current of 110 %, according to the method of the temperature-rise test of IEC 60947-7-1. This is a modification of requirements for such terminals compared to the maximum temperature rise of 45 K allowed by clause 4.2.2.2 of IEC 60079-7 Edition 4. This modification is not given in the table of significant changes between IEC 60079-7 Edition 5.0 and IEC 60079-7 Edition 4, and thus it has not been classified as “minor and editorial” “extension” or ” major technical” change. Question: Shall terminals, certified as Ex components according to IEC 60079-7 Edition 4, be additionally assessed according the new requirements of IEC 60079-7:2015 (Ed. 5.0) concerning the temperature rise of the conductor bar when up-issue of the Ex component certificate is sought by the manufacturer or when the certified Ex component is incorporated into an equipment assessed according to IEC 60079-7:2015 (Ed 5.0)? Answer: Yes because the acceptance criteria (temperature rise) has changed. The decrease of the maximum allowed temperature rise of the conductor bar could, for example, be handled by decrease of the rated current of the terminals previously certified. |  |  |