- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

TITLE: Draft ExTAG Decision Sheet – The tensile force of cable pull test according to IEC 60079-18

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

This proposed Draft ExTAG Decision Sheet ExTAG/460/CD – The tensile force of cable pull test according to IEC 60079-18, has been prepared by NEPSI China.

It is issued for a six week comment period for consideration by ExTAG Members.

Please submit comments using the comments table, a separate document by -

2017 09 18  to

Christine Kane

If there are no comments received the document will be forwarded for publication.

Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

COLLECTION OF IECEx / ExTAG DECISION

| Standard: IEC 60079-18:2014 (Edition 4.0) IEC 60079-18:2009 (Edition 3.0) | Clause: 8.2.5.1 8.2.5.1 |  |
| --- | --- | --- |
| Subject: The tensile force of cable pull test according to IEC 60079-18 Status: Draft | Key words: - Tensile force - cable | Date: 7 July 2017 Originator of proposal: NEPSI TC/SC involved: MT 60079-18 |
| Background: In clause 8.2.5.1 of IEC 60079-18:2014 Edition 4.0, the requirement of the tensile force which shall be applied for cable pull test includes following description: “5 times the mass (in kilograms) of the “m” equipment”. Comparing to the requirement in clause 8.2.5.1 of IEC 60079-18:2009 Edition 3.0, this requirement is described as: “50 times the mass (in kilograms) of the “m” equipment”. This modification is not given in the table of significant changes between IEC 60079-18 Edition 4.0 and IEC 60079-18 Edition 3.0, and thus it has not been classified as “minor and editorial”, “extension” or ” major technical” change. This issue was discussed and requested to clarify during the open forum of 2017 IECEx International Conference held in Shanghai China. Question: Both two editions of the standard IEC 60079-18 can be used to apply for IECEx certificate according to IECEx rules. Considering such obviously difference test requirement, shall the latest standard with requirement of 5 times the mass (in kilograms) of the “m” equipment be applied? Answer: Yes. No matter which version of standard is used to apply for IECEx certificate, the requirement of cable pull test of IEC 60079-18:2014 shall be applied. |  |  |