- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

TITLE: ExTAG/462B/CD Draft ExTAG Decision Sheet – Creepage distance and clearance of on-sparking ballast according to IEC 60079-15

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

This proposed Draft ExTAG Decision Sheet ExTAG/462B/CD –Creepage distance and clearance of on-sparking ballast according to IEC 60079-15, has been prepared by NEPSI China and PTB Germany taking into account comments contained in ExMC/528/CC Compilation of comments and observations on ExTAG/462A/CD.

This updated version is now submitted for discussion during the EXTAG 2018 Cannes Meeting.

Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

COLLECTION OF IECEx / ExTAG DECISION

| Standard: IEC 60079-15:2010 (Edition 4.0) | Clause: 11.2.4.5 11.2.5 |  |
| --- | --- | --- |
| Subject: Creepage distances and clearances of non-sparking ballast in non-sparking luminaire Status: Draft | Key words: - Reduced Creepage distances and clearances - Non-sparking ballast - Non-sparking luminaire | Date: 4 September 2018 Originator of proposal: NEPSI PTB TC/SC involved: |
| Background: IEC 60079-15:2010 Edition 4.0 has addressed the requirement of creeapge distances and clearances in clause 11.2.4.5 and clause 11.2.5 for ballast and non-sparking luminaires by following description: Clause 11.2.4.5 of IEC 60079-15:2010 Edition 4.0 “If the ballast is not protected by an internal over current device on the printed circuit boards of electronic ballasts, the requirements for creepage and clearance distances in Table 3 of IEC 61347-1 apply without the exemptions permitted in that standard. If such an over current device is used the creepage and clearance distances on the supply side of the over current device shall be in line with Table 2. The over current device, if employed, shall have a rated voltage not less than that of the circuit and shall have a breaking capacity not less than the fault current of the circuit.”. Clause 11.2.5 of IEC 60079-15:2010 Edition 4.0 “With exception of the supply terminals for which the creepage and clearance of Table 2 apply, the creepage distance and clearance requirements of the relevant clause of IEC 60598 shall apply.” Question : For non-sparking ballast with over current device, the creepage distance and clearance on the supply side has been specified in the standard clearly. - For those circuit after the over current device, is it essential to verify the creepage distance and clearance? - What are the requirements? Answer: - Yes The concept of non-sparking is to minimize the occurrence of arcs or sparks capable of creating an ignition hazard during conditions of normal operation. Any separations between conductive parts shall be verified. So the creepage distances and clearances after the over current device of the ballast shall be checked according to the requirements of IEC 60079-15:2010. - The creepage distances and clearances shall be checked according to clause 11.2.5 of IEC 60079-15:2010, which requires applying IEC 60598. In IEC 60598, it is written that the distances according to table 11.1 mustn’t apply when IEC publications for parts of the luminaires exist, in case of ballast it is IEC 61347-1:2015. IEC 61347-1:2015 clause 16 has the requirements of creepage distances and clearances. Application of clause 14 or annex P permits reduced distances lower than values of table 7. Two options are available. Option 1: Clause 14 allows sparks and specifies the risk objects like no gas, no flames and no melted metal. The risk of explosions is outside the scope and has to be covered by the requirement of IEC 60079-15 “nA”. Therefore clause 14 is not acceptable for non-sparking ballasts in non-sparking luminaires. Option 2: The non-sparking (nA) ballast with reduced creepage distances and clearances in nonsparking luminaires (nA) shall comply with annex P of IEC 61347-1:2015, in which the distances are shown to be fault tolerant by test. This method is acceptable for non-sparking ballast in non-sparking luminaires (nA). |  |  |