COLLECTION OF IECEx / ExTAG DECISION

| Standard: IEC 60079-0:2017 (Edition 7.0) IEC 60079-0:2011 (Edition 6.0) ISO/IEC 80079-34:2018 | Clause: Table 13 (Note 5) Table 14 (Note 5) Table 11 Table 12 8.4.2 | Draft Decision Sheet: ExTAG/539A/CD |
| --- | --- | --- |
| Subject: Risk of ignition from primary and secondary lithium cells and batteries Status of document: Approved | Key words: - Lithium cells - Lithium batteries - Primary cells - Secondary cells - QAR | - Date: 2019 04 05 Originator of proposal: NANIO CCVE, UL LLC TC/SC involved: IEC/TC 31 WG 22 and WG 37 |
| Question: In Notes 5 of Tables 13 and 14 of IEC 60079-0:2017, a hazard is identified regarding lithium and lithium ion cells as follows: Note 5 of Table 13 of IEC 60079-0:2017: “Recent research has found that some primary Lithium cells of sufficient capacity, particularly cells with a spiral wound construction, can be considered as potentially exothermic chemical reaction ignition sources.” Note 5 of Table 14 of IEC 60079-0:2017: "Recent research has found that some secondary Lithium ion cells of sufficient capacity, particularly cells with a LiCoO2 positive electrode and spiral wound construction, can be considered as potentially strong oxidizers and exothermic chemical reaction ignition sources." While this ignition risk is identified in IEC 60079-0:2017, and is a risk in IEC 60079-0:2011 while not specifically identified, a possible solution to mitigate the risk is not indicated in either edition. When issuing IECEx Test Reports (ExTRs) and Certificates of Conformity (CoCs), how shall this ignition risk be addressed? Answer: In an effort to mitigate the risk of ignition specifically identified in Notes 5 of Tables 13 and 14 of IEC 60079-0:2017, and also of concern in IEC 60079-0:2011, lithium and lithium ion cells shall be confirmed to comply with the requirements of IEC 62133-2, IEC 60086-4 or UL 1642 by one of the following means: - 3rd-party certification of the lithium or lithium ion cells by an IECEE NCB; or - Declaration of conformity of the lithium or lithium ion cells by the cell’s manufacturer. In addition, these cells shall also comply with all applicable requirements in IEC 60079-0, and in the specific IEC 60079 series part(s) included in the product evaluation. During the audit for the QAR, the ExCB shall confirm that the manufacturer is verifying continued conformity of the lithium and lithium ion cells with the requirements of IEC 62133-2, IEC 60086-4 or UL 1642. NOTE The testing and use conditions in the listed battery standards may be less onerous than those required by the Type of Protection standards. Extreme caution should be exercised when exceeding these conditions. |  |  |