INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- TITLE:  Compilation of comments and observations on Draft ExTAG Decision Sheet – ExTAG/544/CD – Revision of ExTAG Decision Sheet 2018/006 – Creepage distances and clearances of non-sparking ballast in non-sparking luminaire

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

This document contains the compilation of comments and observations on ExTAG/544/CD – Revision of ExTAG Decision Sheet 2018/006 – Creepage distances and clearances of non-sparking ballast in non-sparking luminaire, and has been prepared for discussion during the ExTAG 2019 Dubai Meeting.

- Please inform the Secretariat immediately of any omissions or errors at

- Christine Kane

On behalf of Mr. Julien Gauthier

- Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

| ExCB/ ExTL | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation (to be completed by the originator) |
| --- | --- | --- | --- | --- | --- | --- |
| CNEX-Global BV NL | - | - | - | No comments | - | Noted |
| DEK NL |  |  |  | No comments. |  | Noted |
| INERIS FR | Answer 2 | 2nd paragraph | Technical | If the manufacturer only states the compliance with IEC 61347-1 in the documentation, how do we know which clause is applied? If clause 14 or Annex P is applied, the over current device and the creepage and clearance distance on the supply side of this device shall be checked according to IEC 60079-15:2010 Table 2. | 2. The manufacturer shall state the compliance with IEC 61347-1 in the documentation. IEC 61347-1:2015 clause 16 specifies the requirements of creepage distances and clearances. Application of clause 14 or annex P permits reduced distances lower than values of table 7. Both options are applicable. In addition to the statement in the documentation, manufacturer shall provide: - a statement from the ballast’s manufacturer informing which clause is applied, or - the test report of IEC 61347-1. When clause 14 or Annex P is applied, the over current device and creepage and clearance shall be checked according with the requirements of IEC 60079-15:2010. All the evidences used for the assessment shall be added to the schedule drawings (datasheet of the over current device, drawing of the ballast, …). | For discussion in Dubai |
| INERIS FR | Answer 2 | 2nd paragraph | Technical | Does “driver” for LED lights luminaire shall be considered with clause regarding “ballasts” in the assessment? Regarding the assessment of distance, IEC 61347-2-13:2014 for lamp control gear refer to IEC 61347-1:2015. We propose to add a note at the end of the decision sheet regarding the driver’s assessment. | Note: “Drivers” for LED lights luminaire shall be assessed according with IEC 60079-15 §11.2.4.5 in the same way than ballasts: The manufacturer shall state the compliance with IEC 61347-2-13 (lamp control gear) in the documentation. Manufacturer shall provide: - a statement from the driver’s manufacturer informing which clause is applied, or - the test report of IEC 61347-2-13. When clause 14 or Annex P of IEC 61347-1 is applied, an over current device shall be used, and creepage and clearance shall be checked as requested for the ballast in IEC 60079-15:2010. All the evidences used for the assessment shall be added to the schedule drawings (datasheet of the over current device, drawing of the driver, …). | For discussion in Dubai |
| Kiwa NL |  |  | G | No comments | N/A |  |
| NANIO CCVE (ExCB and ExTL) RU |  |  | General | We support the corrected DS ExTAG/544/CD |  | Noted |
| NCC BR | 11.2.4.5 |  |  | We agree. |  | Noted |
| NEPSI CN |  |  | G | We support the revised decision sheet ExTAG/544/CD. |  | Noted |
| TC 31 MT79-15 + MT79-7 + WG40 |  |  |  | We agree with the text of ExTAG/544/CD |  | Noted |
| TIIS JP | Question / Answer |  | G | First, the intent of Question is still not clear. It could be misunderstood. Second, normally ExTL does not verify conformity to other industrial standards which are not addressed in Ex-relevant standards. We think that both clause 14 and Annex P of IEC 61347-1 should be accepted to evaluate creepage and clearance. With this aspect, we support this draft DS rather than DS 2018/006. | Revised Question and Answer as below. Question: In the case of using a ballast that manufacturer has already verified in accordance with IEC 61347-1, are there any additional creepage and clearance requirements for a circuit after over current device? Answer: No | Noted |