| Reference No: |  |  |  |  |  |  |  |  |  |  | #### IEC 60079-2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ## Field of application This form is intended to be used when assessing and testing electrical apparatus for explosive atmospheres according to the standard specified in the adjoining column. The test results are valid for the tested items only. Reproduction This report must not be reproduced other than in its entirety except with the prior written approval of the issuing body | Standard: # IEC 60079-2 Fourth edition 2001-02 Electrical apparatus for explosive gas atmospheres – Pressurized enclosures "p" |  |  |  |  | ## Instructions for use The comment columns can be used to e.g. specify test values, applied alternative requirements/tests or to refer to enclosed additional pages with comments. Abbreviations: N/A = Not applicable (for the assessment/test of the equipment and its design documentation) The applicant is the body/person who has requested the assessment/test and to which the results, as specified in this report, are provided. The short descriptions in the column for "Clause" do not replace the complete text in the standard. |  |  |  |  |  |
|  | Amendments: None |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | This IECEx Test Report may only be used for the IECEx Scheme and must be accompanied by an ExTR cover page issued by an ExCB. |  |  |  |  |  |
| ## Product name |  |  |  |  | # Model/Type designation |  |  |  |  |  |  |
| Serial No | Code (e.g. Ex II T ) |  |  |  |  |  | Ambient temperature [min-max] |  |  |  |  |
| Applicant [name and postal address] |  |  |  |  | Manufactured by [name and postal address] |  |  |  |  |  |  |
| Test sample received [date] |  |  |  |  |  |  |  |  |  |  |  |
| ## Product description |  |  |  |  |  |  |  |  |  |  |  |
| The equipment complies with the standard [yes/no] | ## Prepared by |  |  |  |  |  |  |  |  | Date [year-month-day] |  |
|  | [signature] |  |  |  |  |  |  |  |  |  |  |

Sheet 1 of 56

| Reference No: |  |  |  |  |  |  | IEC 60079-2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 1 | Scope |  |  |  |  |  |  |  |
| 2 See also DS2010/006A | Normative references |  |  |  |  |  |  |  |
| 3 | Terms and definitions |  |  |  |  |  |  |  |
| 4 | Protection types |  |  |  |  |  |  |  |
| 5 | Constructional requirements for pressurized enclosures |  |  |  |  |  |  |  |
| 5.1 | Enclosure |  |  |  |  |  |  |  |
| 5.2 | Materials |  |  |  |  |  |  |  |
| 5.3 | Doors and covers |  |  |  |  |  |  |  |
| 5.3.1 | For group I pressurized enclosures |  |  |  |  |  |  |  |
| 5.3.2 | For group I pressurized enclosures with static pressurization |  |  |  |  |  |  |  |
| 5.3.3 | For group II pressurized enclosures |  |  |  |  |  |  |  |
| 5.3.4 | For group II pressurized enclosures with static pressurization |  |  |  |  |  |  |  |
| 5.3.5 | For type px |  |  |  |  |  |  |  |
| 5.4 | Mechanical strength |  |  |  |  |  |  |  |
| 5.5 | Apertures, partitions, compartments and internal components |  |  |  |  |  |  |  |
| 5.5.1 | Location of apertures and partitions |  |  |  |  |  |  |  |
| 5.5.2 | Internal compartments |  |  |  |  |  |  |  |
| 5.5.3 | Cathode ray tubes or other hermetically sealed devices |  |  |  |  |  |  |  |
| 5.5.4 | Components with small internal free volume |  |  |  |  |  |  |  |
| 5.5.5 | Static pressurization |  |  |  |  |  |  |  |
| 5.6 | Insulating materials for Group I apparatus |  |  |  |  |  |  |  |
| 5.7 | Sealing |  |  |  |  |  |  |  |
| Sheet 2 of 56 Reference No: |  |  |  |  |  |  | IEC 60079-2 |  |

| Clause |  | Results |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Pass | Fail | N/A | Comments | ExCB Review |
| 5.8 | Spark and particle barriers |  |  |  |  |  |
| 6 | Temperature limits |  |  |  |  |  |
| 6.1 | General |  |  |  |  |  |
| 6.2 | For type px or type py |  |  |  |  |  |
| 6.3 | For type pz |  |  |  |  |  |
| 7 | Safety provisions and safety devices (except for static pressurization) |  |  |  |  |  |
| 7.1 | Type of protection or outside hazardous area |  |  |  |  |  |
| 7.2 | Safety related parts of a control system |  |  |  |  |  |
| 7.3 | Provided by manufacturer or user |  |  |  |  |  |
| 7.4 | Functional sequence diagram for type px |  |  |  |  |  |
| 7.5 | Action levels and tolerances |  |  |  |  |  |
| 7.6 | Function during purging |  |  |  |  |  |
| 7.7 | Conditions for proper purging |  |  |  |  |  |
| 7.8 | Operation at too low flow rate |  |  |  |  |  |
| 7.9 | Operation at too low pressure |  |  |  |  |  |
| 7.10 | Minimum overpressure |  |  |  |  |  |
| 7.11 | Separate pressurized enclosures |  |  |  |  |  |
| 7.12 | Interlocking of doors and covers for type px |  |  |  |  |  |
| 7.13 | Type(s) of protection when type px or py not in operation Type(s) of protection when type pz not in operation |  |  |  |  |  |
| 7.14 | Type(s) of protection within type py |  |  |  |  |  |
| 8 | Safety provisions and safety devices for static pressurization |  |  |  |  |  |
| 8.1 | Not capable of causing an explosion |  |  |  |  |  |
| 8.2 | Protective gas |  |  |  |  |  |

Sheet 3 of 56

| Reference No: |  |  |  |  |  |  | IEC 60079-2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 8.3 | Internal sources of release |  |  |  |  |  |  |  |
| 8.4 | Filling of the enclosure |  |  |  |  |  |  |  |
| 8.5 | Number and function of safety devices |  |  |  |  |  |  |  |
| 8.6 | Electrical apparatus within enclosure |  |  |  |  |  |  |  |
| 8.7 | Minimum overpressure |  |  |  |  |  |  |  |
| 9 | Supply of protective gas |  |  |  |  |  |  |  |
| 9.1 | Type of gas |  |  |  |  |  |  |  |
| 9.2 | Temperature |  |  |  |  |  |  |  |
| 10 | Pressurized apparatus with an internal source of release |  |  |  |  |  |  |  |
| 11 | Release conditions |  |  |  |  |  |  |  |
| 11.1 | No release |  |  |  |  |  |  |  |
| 11.2 | Limited release of a gas or vapour |  |  |  |  |  |  |  |
| 11.3 | Limited release of a liquid |  |  |  |  |  |  |  |
| 12 | Design requirements for the containment system |  |  |  |  |  |  |  |
| 12.1 | General design requirements |  |  |  |  |  |  |  |
| 12.2 | Infallible containment system |  |  |  |  |  |  |  |
| 12.3 | Containment system with a limited release |  |  |  |  |  |  |  |
| 13 | Protective gas and pressurizing techniques |  |  |  |  |  |  |  |
| 13.1 | General |  |  |  |  |  |  |  |
| 13.2 | Pressurization with leakage compensation |  |  |  |  |  |  |  |
| 13.2.1 | Leakage compensation and no release |  |  |  |  |  |  |  |
| 13.2.2 | Leakage compensation and limited release of a gas or liquid |  |  |  |  |  |  |  |

Sheet 4 of 56

| Reference No: |  |  |  |  |  |  | IEC 60079-2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 13.3 | Pressurization with dilution |  |  |  |  |  |  |  |
| 13.3.1 | Dilution and no release |  |  |  |  |  |  |  |
| 13.3.2 | Dilution and limited release of a gas or vapour |  |  |  |  |  |  |  |
| 13.3.3 | Dilution and limited release of a liquid |  |  |  |  |  |  |  |
| 14 | Ignition-capable apparatus |  |  |  |  |  |  |  |
| 15 | Internal hot surfaces |  |  |  |  |  |  |  |
| 16 | Type verification and tests |  |  |  |  |  |  |  |
| 16.1 | Maximum overpressure test |  |  |  |  |  |  |  |
| 16.2 | Leakage test |  |  |  |  |  |  |  |
| 16.2.1 | Leakage test (not for static pressurization) |  |  |  |  |  |  |  |
| 16.2.2 | Adjustment to maximum overpressure in case of static pressurization |  |  |  |  |  |  |  |
| 16.3 | Purging test for pressurized enclosures with no internal source of release (pressurization technique may be leakage compensation or continuous flow) and filling procedure test for static pressurization |  |  |  |  |  |  |  |
| 16.3.1 | Purging test for pressurized enclosure where the protective gas is air |  |  |  |  |  |  |  |
| 16.3.2 | Pressurized enclosure where the protective gas is inert |  |  |  |  |  |  |  |
| 16.3.3 | Pressurized enclosure where the protective gas may be either air or an inert gas with a density equal to air 10 % |  |  |  |  |  |  |  |
| 16.3.4 | Filling procedure test for a pressurized enclosure protected by static pressurization |  |  |  |  |  |  |  |
| 16.4 | Purging and dilution tests for a pressurized enclosure with an internal source of release |  |  |  |  |  |  |  |
| 16.4.1 | Test gas |  |  |  |  |  |  |  |
| 16.4.2 | Pressurized enclosure where the flammable substance has less than 2 % (V/V) oxygen and the protective gas is inert |  |  |  |  |  |  |  |

Sheet 5 of 56

| Reference No: |  |  |  |  |  |  | IEC 60079-2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 16.4.2.1 | Purging test |  |  |  |  |  |  |  |
| 16.4.2.2 | Dilution test |  |  |  |  |  |  |  |
| 16.4.3 | Pressurized enclosure with pressurization by continuous flow, containment system with less than 21 % (V/V) oxygen and the protective gas is inert |  |  |  |  |  |  |  |
| 16.4.3.1 | Purging test |  |  |  |  |  |  |  |
| 16.4.3.2 | Dilution test |  |  |  |  |  |  |  |
| 16.4.4 | Pressurized enclosure where the flammable substance is not a liquid, pressurization by continuous flow and the protective gas is air |  |  |  |  |  |  |  |
| 16.4.4.1 | Purging test |  |  |  |  |  |  |  |
| 16.4.4.2 | Dilution test |  |  |  |  |  |  |  |
| 16.5 | Verification of minimum overpressure |  |  |  |  |  |  |  |
| 16.6 | Tests for an infallible containment system |  |  |  |  |  |  |  |
| 16.6.1 | Overpressure test |  |  |  |  |  |  |  |
| 16.6.2 | Infallibility test |  |  |  |  |  |  |  |
| 16.7 | Overpressure test for a containment system with a limited release |  |  |  |  |  |  |  |
| 16.8 | Verifying ability of the pressurized enclosure to limit internal pressure |  |  |  |  |  |  |  |
| 16.8.1 | Enclosure designed for use with compressed air |  |  |  |  |  |  |  |
| 16.8.2 | Testing at maximum rated supply pressure |  |  |  |  |  |  |  |
| 16.8.3 | All openings closed |  |  |  |  |  |  |  |
| 16.8.4 | Internal pressure measured |  |  |  |  |  |  |  |
| 17 | Routine tests |  |  |  |  |  |  |  |

Sheet 6 of 56

| Reference No: |  |  |  |  |  |  | IEC 60079-2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 17.1 | Functional test |  |  |  |  |  |  |  |
| 17.2 | Leakage test |  |  |  |  |  |  |  |
| 17.3 | Tests for an infallible containment system |  |  |  |  |  |  |  |
| 17.4 | Test for a containment system with a limited release |  |  |  |  |  |  |  |
| 18 | Marking |  |  |  |  |  |  |  |
| 18.1 | According to IEC 60079-0 |  |  |  |  |  |  |  |
| 18.2 | Warning markings |  |  |  |  |  |  |  |
| 18.3 | Supplementary information |  |  |  |  |  |  |  |
| 18.4 | Additionally marking if containment system provided |  |  |  |  |  |  |  |
| 18.5 | Static pressurization |  |  |  |  |  |  |  |
| 18.6 | Separate certification |  |  |  |  |  |  |  |
| 18.7 | Valve(s) |  |  |  |  |  |  |  |
| 18.8 | Limited pressure |  |  |  |  |  |  |  |
| 18.9 | Inert gas or protective gas |  |  |  |  |  |  |  |

Sheet 7 of 56

| Section 2 EVALUATION RECORD To be completed by ExTL IEC 60079-2 Fourth edition 2001-02 Electrical apparatus for explosive gas atmospheres - Part 2: Pressurized enclosures "p" |  |
| --- | --- |
| Report |  |
| Reference No. |  |
| Tested by ( + signature) Approved by (+ signature) Date of issue Content |  |
| This report is based on a standard format prepared by CSA International |  |
| Client |  |
| Name Address |  |
| Evaluation Record Form No. ExTR600792/Version 2a/DS Copyright reserved to the bodies participating in the IECEx Scheme |  |
| Testing laboratory |  |
| Name Address Testing location |  |
| Test item Standard IEC 60079-2 Description. Trademark. Model and/or type reference Manufacturer |  |

Sheet 8 of 56

| Test Item (continued) Rating(s) Type of transformers (where relevant) Application Protection index Other characteristics Rated ambient temperature Ta (OC) | stationary / portable / hand-held IP |
| --- | --- |
| Other information |  |

Sheet 9 of 56

General remarks This evaluation record is not valid unless appended to an IECEx Test Report issued by an ExCB, in accordance with IECEx 02. This evaluation record shall not be reproduced except in full without the written approval of the testing laboratory. The test results presented in this evaluation record relate only to the item tested.

Copy of marking plate

Sheet 10 of 56

| MANUFACTURER'S DOCUMENTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Subject | Drawing | Rev. | Date |

Sheet 11 of 56

Evaluation Record

| ## IEC 60079-2 |  | SCOPE, NORMATIVE REFERENCES, TERMS AND DEFINITIONS 1/1 | # APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  | REQUIREMENTS | # YES | NO | ENCL. |  |
| 1 |  | Scope |  |  |  |  |
| 2 |  | Normative references |  |  |  |  |
| 3 |  | Terms and definitions |  |  |  |  |
| Scope |  |  |  |  |  |  |
| The electrical apparatus defined below (see overview) is feasible for coverage in accordance with the specific requirements addressed by this part of IEC 60079: |  |  |  |  |  |  |
|  | YES |  |  |  |  |  |
|  | NO |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |
| Overview: |  |  |  |  |  |  |
| ## Normative references |  |  |  |  |  |  |
| The electrical apparatus has been assessed to the most recent editions of the standards which are referenced and posted as provisions of this part of IEC 60079: |  |  |  |  |  |  |
|  | YES |  |  |  |  |  |
|  | NO |  |  |  |  |  |
|  | Notes |  |  |  |  |  |
| ## Terms and definitions |  |  |  |  |  |  |
|  | All definitions covered in Clause 2 apply, as noted for the specific requirements herein |  |  |  |  |  |
|  | Notes |  |  |  |  |  |

Sheet 12 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  | PROTECTION TYPES 1/3 |  |  |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  | REQUIREMENTS |  |  |  |  | # YES |  | NO |  | ENCL. |  |  |
| 4 |  | Protection types |  |  |  |  |  |  |  |  |  |  |  |
| Protection types |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Table 1 – Determination of protection type |  |  |  |  |  |  |  |  |  |  |  |  |
| Flammable substance in the containment system |  |  |  | External zone classification |  | Enclosure contains ignition-capable apparatus |  |  |  | Enclosure does not contain ignition-capable apparatus |  |  |  |
| No containment system |  |  |  | 1 |  | Type px (a) |  |  |  | Type py |  |  |  |
| No containment system |  |  |  | 2 |  | Type pz |  |  |  | No pressurization required |  |  |  |
| Gas / vapour |  |  |  | 1 |  | Type px (a) |  |  |  | Type py |  |  |  |
| Gas / vapour |  |  |  | 2 |  | Type px ( and ignition- capable apparatus is not located in the dilution area) |  |  |  | Type py (b) |  |  |  |
| Liquid |  |  |  | 1 |  | type px (a) [inert] (c) |  |  |  | Type py |  |  |  |
| Liquid |  |  |  | 2 |  | Type pz [inert] (c) |  |  |  | No pressurization required (d) |  |  |  |
| NOTE: If the flammable substance is liquid, normal release is never permitted. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Protection type px also applies to group I - If no normal release; see annex E - The protective gas shall be inert if "[inert]" is shown after the pressurization type; see clause 13. - Protection by pressurization is not required since it is considered unlikely that a fault causing a release of liquid will simultaneously occur with a fault in the equipment that would provide an ignition source. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 13 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  | PROTECTION TYPES 2/3 |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  | # YES | NO |  |  | ENCL. |  |  |
| 4 |  |  | Protection types (continued) |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Protection types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Table 2 – Design criteria based upon protection type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Design criteria |  |  |  | Type px |  | Type py |  | Type pz with indicator |  |  |  | Type pz with alarm |  |  |  |
| Degree of enclosure protection according to IEC 60529 or IEC 60034-5 |  |  |  | IP 4X minimum |  | IP4X minimum |  | IP4X minimum |  |  |  | IP3X minimum |  |  |  |
| Resistance of enclosure to impact |  |  |  | IEC 60079-0, table 4 |  | IEC 60079-0, table 4 |  | IEC 60079-0, table 4 |  |  |  | IEC 60079-0, half the value of table 4 |  |  |  |
| Verifying purge period |  |  |  | Requires a timing device and monitoring of pressure and flow |  | Time and flow marked |  | Time and flow marked |  |  |  | Time and flow marked |  |  |  |
| Preventing incandescent particles from exiting a normally closed relief vent into a zone 1 area |  |  |  | Spark and particle barrier required, see 5.8, unless incandescent particles not normally produced |  | No requirement (note 1) |  | Spark and particle barrier required, see 5.8, unless incandescent particles not normally produced |  |  |  | Spark and particle barrier required, see 5.8, unless incandescent particles not normally produced |  |  |  |
| Preventing incandescent particles from exiting a normally closed relief vent into a zone 2 area |  |  |  | No requirement (note 2) |  | No requirement (note 2) |  | No requirement (note 2) |  |  |  | No requirement (note 2) |  |  |  |
| Preventing incandescent particles from exciting a vent open to a zone 1 area in normal operation |  |  |  | Spark and particle barrier required, see 5.8 |  | Spark and particle barrier required, see 5.8 |  | Spark and particle barrier required, see 5.8 |  |  |  | Spark and particle barrier required, see 5.8 |  |  |  |

Sheet 14 of 56	(IEC 60079-2, 2001-02)

| ## IEC 60079-2 |  |  | PROTECTION TYPES 3/3 |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  | # YES | NO |  |  | ENCL. |  |  |
| 4 |  |  | Protection types (continued) |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Protection types |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Table 2 – Design criteria based upon protection type (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Design criteria |  |  |  | Type px |  | Type py |  | Type pz with indicator |  |  |  | Type pz with alarm |  |  |  |
| Preventing incandescent particles from exciting a vent open to a zone 2 area in normal operation |  |  |  | Spark and particle barrier required, see 5.8, unless incandescent particles not normally produced |  | No requirement (note 1) |  | Spark and particle barrier required, see 5.8, unless incandescent particles not normally produced |  |  |  | Spark and particle barrier required, see 5.8, unless incandescent particles not normally produced |  |  |  |
| Door / cover requiring a tool to remove |  |  |  | Warning, see 5.3 and 6.2 b) ii) |  | Warning, see 5.3 (note 1) |  | Warning, see 5.3 and 6.2 b) ii) |  |  |  | Warning, see 5.3 and 6.2 b) ii) |  |  |  |
| Door / cover not requiring a tool to remove |  |  |  | Interlock, see 7.12 (no internal hot parts) |  | Warning, see 5.3 (note 1) |  | No requirement (note 3) |  |  |  | No requirement (note 3) |  |  |  |
| Internal hot parts that require a cool-down period before opening enclosure |  |  |  | Comply with 6.2 b) ii) |  | Not applicable |  | Warning, see 5.3 and 6.2 b) ii) |  |  |  | Warning, see 5.3 and 6.2 b) ii) |  |  |  |
| NOTE 1 Subclause 6.2 b) ii) is not applicable for type py since neither hot internal parts nor normally created incandescent particles are permitted NOTE 2 There is no requirement for spark and particle barriers since in abnormal operation, where the relief vent opens, it is unlikely that the external atmosphere is within the explosive limits NOTE 3 There is no requirement for marking or tool accessibility on a pz enclosure since in normal operation the enclosure is pressurized with all covers and doors in place. If a cover or door is removed, it is unlikely that the atmosphere is within the explosive limits. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 15 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | CONSTRUCTIONAL REQUIREMENTS FOR PRESSURIZED ENCLOSURES 1/5 |  |  |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  | # YES | NO |  | ENCL. |  |  |  |
| 5.1 |  |  |  | Enclosure |  |  |  |  |  |  |  |  |  |  |  |
| 5.2 |  |  |  | Materials |  |  |  |  |  |  |  |  |  |  |  |
| 5.3 |  |  |  | Doors and covers |  |  |  |  |  |  |  |  |  |  |  |
| 5.3.1 |  |  |  | For group I pressurized enclosures |  |  |  |  |  |  |  |  |  |  |  |
| 5.3.2 |  |  |  | For group I pressurized enclosures with static pressurization |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Degree of protection in accordance with table 2 |  |  |  |  |  | IP |  |  |  |  |  |  |  |  |
| ### Materials |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Are not adversely affected by the specified protective gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### For group I pressurized enclosures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Special fasteners comply with 9.2 of IEC 60079-0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Interlocked so that electrical apparatus with no type of protection is disconnected automatically |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Supply cannot be restored until doors and covers are closed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The requirements of 7.6 for the safety devices are applied |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### For group I pressurized enclosures with static pressurization |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Special fasteners comply with 9.2 of IEC 60079-0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Warning provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 16 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | CONSTRUCTIONAL REQUIREMENTS FOR PRESSURIZED ENCLOSURES 2/5 |  |  |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  | # YES | NO |  | ENCL. |  |  |  |
| 5.3.3 |  |  |  | For group II pressurized enclosures |  |  |  |  |  |  |  |  |  |  |  |
| 5.3.4 |  |  |  | For group II pressurized enclosures with static pressurization |  |  |  |  |  |  |  |  |  |  |  |
| 5.3.5 |  |  |  | For type px |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### For group II pressurized enclosures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Can be opened only by the use of a tool or key: |  |  |  |  |  |  | YES |  |  | NO |  |  |  |  |
|  | If NO: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Interlocked so that electrical apparatus with no type of protection is disconnected automatically |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Supply cannot be restored until doors and covers are closed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### For group II pressurized enclosures with static pressurization |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Can only be opened by the use of a tool |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Warning provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### For type px |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Pressurized enclosure contains hot parts requiring a cool-down. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | YES |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | NO |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Enclosure can only be opened by the use of a key or tool |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 17 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  |  | CONSTRUCTIONAL REQUIREMENTS FOR PRESSURIZED ENCLOSURES 3/5 |  |  |  | # APPLIED |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  | # YES |  |  | NO |  |  |  | ENCL. |  |  |  |
| 5.4 |  |  |  |  | Mechanical strength |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.1 |  |  |  |  | Location of apertures and partitions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.2 |  |  |  |  | Internal compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Mechanical strength |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The pressurized enclosure ducts and their connecting parts withstand a pressure of: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 1,5 times the overpressure specified by the manufacturer: |  |  |  |  |  |  |  |  |  |  |  |  | Pa |  |  |  |  |
|  |  | or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | the minimum value of 200 Pa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Pressure can occur in service that can cause deformation: |  |  |  |  |  | YES |  |  |  |  |  | NO |  |  |  |  |  |
|  |  | If YES: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Safety device provided that limits the overpressure: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Apparatus is marked "X": and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Descriptive documents contain all necessary information for the user: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Location of apertures and partitions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Effective purging is ensured. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Internal compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Internal compartments are: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | vented to the main enclosure or separately purged |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 18 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  |  | CONSTRUCTIONAL REQUIREMENTS FOR PRESSURIZED ENCLOSURES 4/5 |  |  | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  | REQUIREMENTS |  |  | # YES | NO | ENCL. |  |  |
| 5.5.3 |  |  |  |  | Cathode ray tubes or other hermetically sealed devices |  |  |  |  |  |  |  |
| 5.5.4 |  |  |  |  | Components with small internal volume |  |  |  |  |  |  |  |
| 5.5.5 |  |  |  |  | Static pressurization |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Cathode ray tubes or other hermetically sealed devices |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Cathode ray tubes or other hermetically sealed devices provided which do not require purging. |  |  |  |  |  |  |  |  |  |  |
|  |  | Notes: |  |  |  |  |  |  |  |  |  |  |
| ### Components with small internal volume |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Components with a free internal volume less than 20 cm³ |  |  |  |  |  |  |  |  |  |  |
|  |  | and |  |  |  |  |  |  |  |  |  |  |
|  |  | Total volume less than 1 % of the free internal volume of the pressurized apparatus |  |  |  |  |  |  |  |  |  |  |
| ### Static pressurization |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | One or more aperture(s) provided |  |  |  |  |  |  |  |  |  |  |
|  |  | and |  |  |  |  |  |  |  |  |  |  |
|  |  | After filling and pressurization all apertures are closed |  |  |  |  |  |  |  |  |  |  |

Sheet 19 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | CONSTRUCTIONAL REQUIREMENTS FOR PRESSURIZED ENCLOSURES 5/5 |  | # APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  | # YES | NO | ENCL. |  |  |  |
| 5.6 |  |  |  | Insulating materials for group I apparatus |  |  |  |  |  |  |  |
| 5.7 |  |  |  | Sealing |  |  |  |  |  |  |  |
| 5.8 |  |  |  | Spark and particle barriers |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |
| Insulating materials for group I apparatus |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Subjected to electrical stresses capable of causing arcs in air and rated current more than 16 A |  |  |  |  |  |  |  |  |  |
|  |  | then: |  |  |  |  |  |  |  |  |  |
|  |  | CTI  400 M according to IEC 60112 |  |  |  |  |  |  |  |  |  |
|  |  | and/or |  |  |  |  |  |  |  |  |  |
|  |  | Detector for possible decomposition that |  |  |  |  |  |  |  |  |  |
|  |  | automatically disconnects power supply and the |  |  |  |  |  |  |  |  |  |
|  |  | presence and function verified |  |  |  |  |  |  |  |  |  |
|  |  | and/or |  |  |  |  |  |  |  |  |  |
|  |  | Creepage distances according to material group III of pollution degree 3 in table 4 of IEC 60664-1 |  |  |  |  |  |  |  |  |  |
| ### Sealing |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Cable and conduit entries are sealed to maintain IP rating |  |  |  |  |  |  |  |  |  |
|  |  | or |  |  |  |  |  |  |  |  |  |
|  |  | Unsealed cable and conduit entries are considered as part of the enclosure |  |  |  |  |  |  |  |  |  |
| ### Spark and particle barriers |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Incandescent particles are not normally produced since make/break contacts operate at less than 10 A and the working voltage does not exceed either 275 Vac or 60 Vdc and the contacts have a cover. |  |  |  |  |  |  |  |  |  |
|  |  | Spark and particle barrier is not provided since the normally closed relief vent exhausts into a Zone 1 area and incandescent particles are not normally produced |  |  |  |  |  |  |  |  |  |
|  |  | Spark and particle barrier is not provided because of exhausting into a Zone 2 area and incandescent particles are not normally produced |  |  |  |  |  |  |  |  |  |
|  |  | Spark and particle barrier provided |  |  | Spark and particle barrier not provided;marking in accordance with 27.2 i) of IEC 60079-0: |  |  |  |  |  |  |

Sheet 20 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | TEMPERATURE LIMITS 1/1 |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  | # YES |  | NO |  | ENCL. |  |  |  |
| 6.1 |  |  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.2 |  |  |  | ### For type px or py |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.3 |  |  |  | ### For type pz |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Temperature class: T |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### For type px or py |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The temperature class is based on: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | the hottest external surface of the enclosure |  |  |  |  |  | the hottest internal component surface |  |  |  |  |  |  |  |  |  |
|  |  | Internal component exceeds marked temperature class: |  |  |  |  |  |  | YES |  |  |  | NO |  |  |  |  |
|  |  | If YES then: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Internal component complies with 5.3 of IEC 60079-0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | enclosure marked with cool-down time: and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | appropriate measures taken if pressurization ceases: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### For type pz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Temperature class based on the hottest external surface of the enclosure. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 21 of 56	(IEC 60079-2, 2001-02)

| ## IEC 60079-2 |  |  |  | SAFETY PROVISIONS AND SAFETY DEVICES (EXCEPT FOR STATIC PRESSURIZATION) 1/7 |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  | # YES |  | NO |  | ENCL. |  |  |
| 7.1 |  |  |  | Type of protection or outside hazardous area |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Table 3 – Safety devices based upon protection type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Design criteria |  |  |  |  |  | Type px |  |  | Type py |  |  |  | Type pz |  |  |  |
| Safety device to detect loss of minimum overpressure |  |  |  |  |  | Pressure sensor, see 7.9 |  |  | Pressure sensor, see 7.9 |  |  |  | Indicator or pressure sensor, see 7.9 d) |  |  |  |
| Safety device(s) to verify purge period |  |  |  |  |  | Timing device, pressure sensor and flow sensor at outlet, see 7.6 |  |  | Time and flow marked, see 7.7 c) |  |  |  | Time and flow marked, see 7.7 c) |  |  |  |
| Safety device for a door or cover that requires a tool to open |  |  |  |  |  | Warning, see 6.2 b) |  |  | Warning, see 6.2 b) |  |  |  | No requirement |  |  |  |
| Safety device for a door or cover that does not require a tool to open |  |  |  |  |  | Interlock, see 7.12 (no internal hot parts) |  |  | Warning, see 6.2 b) (no internal hot parts) |  |  |  | Warning, see 6.2 b) |  |  |  |
| Safety device for hot internal parts when there is a containment system (see clause 15) |  |  |  |  |  | Alarm and stop flow of flammable substance |  |  | Not applicable for protection type since internal hot parts not permitted |  |  |  | Alarm (normal release not permitted) |  |  |  |
|  |  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Type of protection or outside hazardous area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Safety devices: |  |  |  |  |  |  |  | have a suitable type of protection or |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | are mounted outside hazardous area |  |  |  |  |  |  |  |

Sheet 22 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  | SAFETY PROVISIONS AND SAFETY DEVICES (EXCEPT FOR STATIC PRESSURIZATION) 2/7 |  |  |  |  | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  |  |  | # YES | NO | ENCL. |  |  |
| 7.2 |  |  | Safety related parts of a control system |  |  |  |  |  |  |  |  |  |
| 7.3 |  |  | Provided by manufacturer or user |  |  |  |  |  |  |  |  |  |
| 7.4 |  |  | Funtional sequence diagram for type px |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Safety related parts of a control system |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Safety and integrity of the control system is consistent: * |  |  |  | with for type px a single fault evaluation |  |  |  |  |  |  |  |
|  |  |  |  |  | with for type py a single fault evaluation |  |  |  |  |  |  |  |
|  |  |  |  |  | with for type pz, normal operation |  |  |  |  |  |  |  |
|  | * responsibility of the manufacturer |  |  |  |  |  |  |  |  |  |  |  |
| ### Provided by manufacturer or user |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Safety devices provided by: |  |  |  |  | manufacturer |  |  |  |  |  |  |
|  |  |  |  |  |  | user |  |  |  |  |  |  |
|  | Safety devices not provided by manufacturer, then: |  |  |  |  | apparatus marked with "X" and |  |  |  |  |  |  |
|  |  |  |  |  |  | descriptive documents with necessary information |  |  |  |  |  |  |
| ### Funtional sequence diagram for type px |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The functional sequence diagram: * |  |  |  |  |  | clearly identifies and shows the operational states of the safety devices and ensuing actions |  |  |  |  |  |
|  |  |  |  |  |  |  | is in conformity with the sequence diagram as shown by functional tests |  |  |  |  |  |
|  |  |  |  |  |  |  | has been tested under normal atmospheric conditions |  |  |  |  |  |
|  |  |  |  |  |  |  | has been tested under conditions specified by the manufacturer |  |  |  |  |  |
|  | * provided by the manufacturer |  |  |  |  |  |  |  |  |  |  |  |

Sheet 23 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  | SAFETY PROVISIONS AND SAFETY DEVICES (EXCEPT FOR STATIC PRESSURIZATION) 3/7 |  |  |  |  | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  |  |  | # YES | NO | ENCL. |  |  |
| 7.5 |  |  | Action levels and tolerances |  |  |  |  |  |  |  |  |  |
| 7.6 |  |  | Function during purging |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Action levels and tolerances |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Of the safety devices the following is specified * : |  |  |  |  |  | maximum action levels |  |  |  |  |  |
|  |  |  |  |  |  |  | minimum action levels |  |  |  |  |  |
|  |  |  |  |  |  |  | tolerances |  |  |  |  |  |
|  |  |  |  |  |  |  | used within normal operational limits * |  |  |  |  |  |
|  | * specified by the manufacturer |  |  |  |  |  |  |  |  |  |  |  |
| ### Function during purging |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Safety devices provided to prevent electrical apparatus within pressurized enclosure becoming energised until purging has been completed: |  |  |  |  |  |  |  |  |  |  |
|  |  | For type px, the sequence of operations is as follows: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1 | following the initiation of the sequence, the purging flow and the overpressure are monitored |  |  |  |  |  |  |  |
|  |  |  |  | 2 | the purge timer is started when the minimum flow rate and the overpressure are within the specified limits |  |  |  |  |  |  |  |
|  |  |  |  | 3 | after expiry of time, electrical apparatus available to be energised |  |  |  |  |  |  |  |
|  |  |  |  |  | on failure of any step in sequence, the circuit will be reset to the beginning |  |  |  |  |  |  |  |
|  |  |  |  | 4 |  |  |  |  |  |  |  |  |
|  |  | Notes: |  |  |  |  |  |  |  |  |  |  |

Sheet 24 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  | SAFETY PROVISIONS AND SAFETY DEVICES (EXCEPT FOR STATIC PRESSURIZATION) 4/7 |  |  |  |  |  |  | # APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  | REQUIREMENTS |  |  |  |  |  |  | # YES | NO | ENCL. |  |
| 7.7 |  | Conditions for proper purging |  |  |  |  |  |  |  |  |  |  |
| Items: |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Conditions for proper purging |  |  |  |  |  |  |  |  |  |  |  |  |
|  | For type px or py the following is specified by the manufacturer: |  |  |  |  | minimum purge flow and time to satisfy the purging / dilution test in 16.3 or 16.4 |  |  |  |  |  |  |
|  |  |  |  |  | or |  |  |  |  |  |  |  |
|  |  |  |  |  |  | five-enclosure-volume purge without testing |  |  |  |  |  |  |
|  | Minimum purge flow: |  | l/min. |  |  |  |  |  |  |  |  |  |
|  | Purge time: |  | min. |  |  |  |  |  |  |  |  |  |
|  | For type pz the purging time is specified by the manufacturer: |  |  |  |  | the minimum purge flow for five- enclosure-volume purging or reduced quantity of protective gas since effective purging is demonstrated by the tests in 16.3 or 16.4 |  |  |  |  |  |  |
|  | Minimum purge flow: |  | l/min. |  |  |  |  |  |  |  |  |  |
|  | Purge time: |  | min. |  |  |  |  |  |  |  |  |  |
|  | For type px: |  |  | the actual purging flow rate is monitored at the outlet of the pressurized enclosure |  |  |  |  |  |  |  |  |
|  | ## For type py or pz: |  |  | the purging flow rate is monitored at the outlet of the pressurized enclosure |  |  |  |  |  |  |  |  |
|  |  |  |  | or |  |  |  |  |  |  |  |  |
|  |  |  |  | the flow is deduced from enclosure pressure and a defined orifice at the outlet |  |  |  |  |  |  |  |  |
|  |  |  |  | instruction label for purging provided |  |  |  |  |  |  |  |  |

Sheet 25 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  | SAFETY PROVISIONS AND SAFETY DEVICES (EXCEPT FOR STATIC PRESSURIZATION) 5/7 |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  | # YES | NO | ENCL. |  |  |  |
| 7.8 |  |  | Operation at too low flow rate |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.9 |  |  | Operation at too low pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Operation at too low flow rate |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Minimum flow rate specified by manufacturer: |  |  |  |  |  |  | YES |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | NO |  |  |  |  |  |  |  |  |
|  |  | If yes, one or more automatic safety devices provided |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Operation at too low pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | One or more automatic safety devices provided |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Automatic safety device sensor takes its signal directly from the pressurized enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | No valves between the automatic safety device sensor and the pressurized enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Correct operation of the safety devices can be checked |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Location and setting take into account the requirements of 7.10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Type pz is equipped with: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | automatic safety device |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | indicator |  |  |  |  |  |  |  |  |  |  |
|  |  | If equipped with indicator, then: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Protective gas supply is equipped with alarm to indicate failure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | No devices between pressurized enclosure and the protective gas supply alarm (except isolating valve and/or pressure- / flow controlling mechanism) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Isolating valves: |  |  | are marked as required in 18.7 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | are capable of being sealed or secured in the open position |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | have an open- or close indication |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | are located immediately adjacent to the pressurized enclosure |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | are used only during servicing of the pressurized enclosure |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 26 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | SAFETY PROVISIONS AND SAFETY DEVICES (EXCEPT FOR STATIC PRESSURIZATION) 6/7 |  |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | # YES |  | NO | ENCL. |  |  |  |
| 7.10 |  |  |  | Minimum overpressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.11 |  |  |  | Separate pressurized enclosures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Minimum overpressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | For type px and type py: |  |  |  |  |  | Pa |  |  |  |  |  |  |  | (at least 50 Pa) |  |  |  |  |  |
|  | For type pz: |  |  |  |  |  | Pa |  |  |  |  |  |  |  | (at least 25 Pa) |  |  |  |  |  |
|  | The following is specified by the manufacturer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Minimum overpressure in service |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Maximum overpressure in service |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Maximum leakage rate at the maximum overpressure |  |  |  |  |  |  |  |  |  |  |  |
|  | Distribution of pressure in different systems and ducts is illustrated in figures C.1 to C.4. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Separate pressurized enclosures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Source of protective gas is common to a number of separate pressurized enclosures: |  |  |  |  |  |  |  |  | YES |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | NO |  |  |  |  |  |  |  |  |  |
|  |  | Each pressurized enclosure provided with safety device: |  |  |  |  |  |  |  |  | YES |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | NO |  |  |  |  |  |  |  |  |  |
|  |  | If common safety device, then resulting control takes account of the most unfavourable configuration. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Common safety device fitted and switches of all electrical apparatus or initiates alarm: |  |  |  |  |  |  |  |  |  |  | YES |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | NO |  |  |  |  |  |  |  |
|  |  | If no, then: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | for type px, the opening of the door or cover is proceded by disconnecting the supply in the particular enclosure, except if permitted by 7.13 and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | the common safety device continues to monitor the overpressure in, and where necessary the flow through, all other pressurized enclosures and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | the subsequent connecting of the supply in the particular pressurized enclosure is preceded by the purging procedure specified in 7.6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 27 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  |  |  |  | SAFETY PROVISIONS AND SAFETY DEVICES (EXCEPT FOR STATIC PRESSURIZATION) 7/7 |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  |  |  | REQUIREMENTS |  |  | # YES |  | NO |  | ENCL. |  |  |
| 7.12 |  |  |  |  |  |  | Interlocking of doors and covers for type px |  |  |  |  |  |  |  |  |  |
| 7.13 |  |  |  |  |  |  | Types of protection when type px or type py not in operation Types of protection when type pz not in operation |  |  |  |  |  |  |  |  |  |
| 7.14 |  |  |  |  |  |  | Types of protection within type py |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Interlocking of doors and covers for type px |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Doors and covers can be opened only by the use of a tool or key and warning label is provided |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | if not, then |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | door and covers are interlocked so that power supply is disconnected automatically when opened and |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | supply cannot be restored until doors and covers are closed and |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | requirements of 7.6 for the safety devices are fulfilled |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Types of protection when type px or type py not in operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Type(s) of protection for electrical apparatus: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | "d" |  |  |  | "m" |  |  |  |
|  |  |  |  |  |  |  |  |  | "e" |  |  |  | "o" |  |  |  |
|  |  |  |  |  |  |  |  |  | "i" |  |  |  | "q" |  |  |  |
| ### Types of protection when type pz not in operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Type(s) of protection for electrical apparatus: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | "d" |  |  |  | "o" |  |  |  |
|  |  |  |  |  |  |  |  |  | "e" |  |  |  | "q" |  |  |  |
|  |  |  |  |  |  |  |  |  | "i" |  |  |  | "nA" |  |  |  |
|  |  |  |  |  |  |  |  |  | "m" |  |  |  | "nC" |  |  |  |
| ### Types of protection within type py |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ### Type(s) of protection for electrical apparatus: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | "o" |  |  |  | "m" |  |  |  |
|  |  |  |  |  |  |  |  |  | "q" |  |  |  | "e" |  |  |  |
|  |  |  |  |  |  |  |  |  | "d" |  |  |  | "nA" |  |  |  |
|  |  |  |  |  |  |  |  |  | "i" |  |  |  | "nC" |  |  |  |

Sheet 28 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | SAFETY PROVISIONS AND SAFETY DEVICES FOR STATIC PRESSURIZATION 1/2 |  |  |  |  |  |  | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  | # YES | NO | ENCL. |  |  |
| 8.1 |  |  |  | Not capable of causing an explosion |  |  |  |  |  |  |  |  |  |  |  |
| 8.2 |  |  |  | Protective gas |  |  |  |  |  |  |  |  |  |  |  |
| 8.3 |  |  |  | Internal source of release |  |  |  |  |  |  |  |  |  |  |  |
| 8.4 |  |  |  | Filling of the enclosure |  |  |  |  |  |  |  |  |  |  |  |
| 8.5 |  |  |  | Number and function of safety devices |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Not capable of causing an explosion |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Safety devices are not capable of causing an explosion |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Electrically operated safety devices: |  |  |  |  |  |  | have a type of protection recognized in IEC 60079-0 or |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | are mounted outside the hazardous area |  |  |  |  |  |  |  |
| ### Protective gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The protective gas: |  |  |  |  | is inert and |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | the concentration of oxygen after filling is less than 1 % by volume |  |  |  |  |  |  |  |  |  |
| Internal source of release |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | No internal source of release |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Filling of the enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Enclosure is filled with inert gas: |  |  |  |  |  |  | in non-hazardous area using |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | procedure specified by manufacturer |  |  |  |  |  |  |  |
| ### Number and function of safety devices |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Number of automatic safety devices provided to operate when overpressure below minimum value: |  |  |  |  |  |  |  |  | 2 (for type px or type py) |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 1 (for type pz) |  |  |  |  |  |

Sheet 29 of 56	(IEC 60079-2, 2001-02)

| ## IEC 60079-2 |  |  |  | SAFETY PROVISIONS AND SAFETY DEVICES FOR STATIC PRESSURIZATION 2/2 SUPPLY OF PROTECTIVE GAS 1/2 |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | # YES | NO | ENCL. |  |  |
| 8.5 |  |  |  | Number and function of safety devices (continued) |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.6 |  |  |  | Electrical apparatus within enclosure |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.7 |  |  |  | Minimum overpressure |  |  |  |  |  |  |  |  |  |  |  |  |
| 9.1 |  |  |  | Type of gas |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety provisions and safety devices for static pressurization Number and function of safety devices (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The automatic safety devices: |  |  |  |  |  |  |  | can be checked on correct operation when in service |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | are only capable of being reset by the use of a tool or key |  |  |  |  |  |  |  |
| ### Safety provisions and safety devices for static pressurization ### Electrical apparatus within enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Electrical apparatus have a type of protection listed in 7.13 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Safety provisions and safety devices for static pressurization ### Minimum overpressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The minimum overpressure: |  |  |  |  |  |  |  |  |  | is greater than the maximum pressure loss in normal service over a period not less than 100 times the time necessary for cooling of the enclosed components in accordance with 6.2 of IEC 60079-0, with a minimum of 1 h and |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | is not less tha 50 Pa over the external pressure under the most onerous conditions specified for normal service |  |  |  |  |  |
| ### Supply of protective gas ### Type of gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The protective gas is: |  |  |  |  |  |  | non-flammable |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | specified by the manufacturer with alternative(s) if applicable |  |  |  |  |  |  |  |  |
|  | Protective gas(es) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 30 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | SUPPLY OF PROTECTIVE GAS 2/2 PRESSURIZED APPARATUS WITH AN INTERNAL SOURCE OF RELEASE 1/8 RELEASE CONDITIONS 1/2 |  |  |  |  | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  | # YES | NO | ENCL. |  |  |
| 9.2 |  |  |  | Temperature |  |  |  |  |  |  |  |  |  |
| 10, 11.1, 11.1.1 and 11.1.2 |  |  |  | No release |  |  |  |  |  |  |  |  |  |
| 10, 11.2 |  |  |  | Limited release of a gas or vapour |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Supply of protective gas ### Temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The temperature of the protective gas: |  |  |  |  |  |  | is  40 C |  |  |  |  |  |
|  |  |  |  |  |  |  |  | is permitted to be > 40 C and marked on the enclosure |  |  |  |  |  |
|  |  |  |  |  |  |  |  | is required to be below a specific temperature and marked on the enclosure |  |  |  |  |  |
| ### Pressurized apparatus with an internal source of release, release conditions ### No release |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | No internal release because: |  |  |  |  | Containment system is infallible, see 12.2 |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Flammable substance inside containment system is in gas or vapour phase operating between specified temperature limits and either |  |  |  |  |  |  |  |
|  |  |  |  |  |  | the gas mixture within the containment system is always below LEL; or |  |  |  |  |  |  |  |
|  |  |  |  |  |  | the minimum pressure inside the pressurized enclosure is at least 50 Pa higher than containment system and |  |  |  |  |  |  |  |
|  |  |  |  |  |  | automatic safety device operates if pressure difference below 50 Pa |  |  |  |  |  |  |  |
|  |  | Apparatus marked with “X” in accordance with 27.2 I) of IEC 60079-0. |  |  |  |  |  |  |  |  |  |  |  |
| ## Pressurized apparatus with an internal source of release, release conditions ## Limited release of a gas or vapour |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The rate of release of the flammable substance into the pressurized enclosure is predictable in all conditions of containment system failure; see 12.3. |  |  |  |  |  |  |  |  |  |  |  |

Sheet 31 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | PRESSURIZED APPARATUS WITH AN INTERNAL SOURCE OF RELEASE 2/8 RELEASE CONDITIONS 2/2 DESIGN REQUIREMENTS FOR THE CONTAINMENT SYSTEM 1/3 |  |  |  |  |  | # APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  | # YES | NO | ENCL. |  |  |  |
| 10, 11.3 |  |  |  | Limited release of a liquid |  |  |  |  |  |  |  |  |  |  |  |
| 10, 12.1 |  |  |  | General design requirements |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Pressurized apparatus with an internal source of release, release conditions ### Limited release of a liquid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The rate of release of the flammable substance into the pressurized enclosure is predictable in all conditions of containment system failure; see 12.3. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Oxygen is released from the liquid and the maximum flow rate is predicted; see 13.2.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Pressurized apparatus with an internal source of release, design requirements for ### the containment system ### General design requirements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The design and construction is based on the most onerous conditions of service |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The containment system is: |  |  |  |  | infallible or |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | has a limited release upon failure |  |  |  |  |  |  |  |  |  |
|  | Flammable substance is a liquid and: |  |  |  |  |  |  | there is no normal release |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | and the protective gas is inert |  |  |  |  |  |  |  |
|  |  | The maximum inlet pressure to the containment system is specified by the manufacturer: |  |  |  |  |  |  | Pa |  |  |  |  |  |  |
|  | The containment system is classified as: |  |  |  |  |  |  | infallable containment system; see 12.2 |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | containment system with a limited release; see 12.3 |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 32 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | PRESSURIZED APPARATUS WITH AN INTERNAL SOURCE OF RELEASE 3/8 DESIGN REQUIREMENTS FOR THE CONTAINMENT SYSTEM 2/3 |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | # YES | NO | ENCL. |  |  |
| 10, 12.2 |  |  |  | Infallible containment system |  |  |  |  |  |  |  |  |  |  |  |  |
| 10, 12.3 |  |  |  | Containment system with a limited release |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Infallible containment system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The containment system is composed of tubes or vessels made of: |  |  |  |  |  |  | metallic |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | ceramic or glass |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | with no moving joints |  |  |  |  |  |  |  |  |
|  | Joints are made by: |  |  |  |  | welding |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | brazing |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | glass to metal sealing |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | eutectic methods, except low temperature alloys like lead/tin composites |  |  |  |  |  |  |  |  |  |  |
| ### Containment system with a limited release |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The design of the containment system is such that the rate of release is predictable in all conditions of containment system failure by means of appropriate flow limiting devices, fitted outside the pressurized enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The quantity of flammable substance released into the pressurized enclosure includes: |  |  |  |  |  |  |  |  |  | the quantity of flammable substance in the containment system and |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | the flow of the flammable substance entering the containment system from the process |  |  |  |  |  |
|  | The flow is limited to a predictable rate by: |  |  |  |  |  |  |  | appropriate flow limiting devices, |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | fitted outside the pressurized enclosure |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | or |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | fitted inside the pressurized enclosure and |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | part between entry of pressurized enclosure and flow limiting device is infallible and |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | flow limiting device is permanently secured and |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | flow limiting device has no movable parts |  |  |  |  |  |  |  |

Sheet 33 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  | PRESSURIZED APPARATUS WITH AN INTERNAL SOURCE OF RELEASE 4/8 DESIGN REQUIREMENTS FOR THE CONTAINMENT SYSTEM 3/3 |  |  |  |  |  | # APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  | REQUIREMENTS |  |  |  |  |  | # YES | NO | ENCL. |  |
| 10, 12.3 |  | Containment system with a limited release (cont.) |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |
| Containment system with a limited release (continued) |  |  |  |  |  |  |  |  |  |  |  |
|  | Process flow into the containment system is limited: |  |  |  | YES |  |  |  |  |  |  |
|  |  |  |  |  | NO |  |  |  |  |  |  |
|  | Process flow into the containment system is not limited and: |  |  | containment system comprises connected parts which individually meet 12.2 and |  |  |  |  |  |  |  |
|  |  |  |  | maximum release of the joints can be predicted and |  |  |  |  |  |  |  |
|  |  |  |  | joints are permanently secured |  |  |  |  |  |  |  |
|  |  |  | and/or |  |  |  |  |  |  |  |  |
|  |  |  |  | containment system includes orifices or nozzles to obtain release in normal operation or |  |  |  |  |  |  |  |
|  |  |  |  | are infallible (12.2) |  |  |  |  |  |  |  |
|  | Flow limiting device is part of the apparatus: |  |  |  |  |  | YES |  |  |  |  |
|  |  |  |  |  |  |  | NO |  |  |  |  |
|  | Flow limiting device is not part of the apparatus and: |  |  | pressurized enclosure is marked "X" and |  |  |  |  |  |  |  |
|  |  |  | special conditions include of the flammable substance into the containment system: |  |  |  |  |  |  |  |  |
|  |  |  |  | the maximum flow and |  |  |  |  |  |  |  |
|  |  |  |  | the maximum pressure |  |  |  |  |  |  |  |
|  | Pressurized enclosure(s) contain a flame: |  |  |  |  |  | YES |  |  |  |  |
|  |  |  |  |  |  |  | NO |  |  |  |  |
|  | Pressurized enclosure(s) contain a flame and: |  |  |  |  |  | pressurized enclosure is assessed as though the flame had been extinguished and |  |  |  |  |
|  |  |  |  |  |  |  | maximum quantity of fuel/air of flame is added to release from containment system |  |  |  |  |

Sheet 34 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | PRESSURIZED APPARATUS WITH AN INTERNAL SOURCE OF RELEASE 5/8 PROTECTIVE GAS AND PRESSURIZING TECHNIQUES 1/3 |  |  |  |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  | # YES |  |  | NO | ENCL. |  |  |  |  |
| 10, 13.1 |  |  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Table 4 – Protective gas requirements for a pressurized enclosure with a containment system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Internal release (see annex E) |  |  |  |  |  |  |  |  |  |  | Continuous dilution |  |  |  |  |  | Leakage compensation |  |  |  |  |  |  |
|  | Substance |  | Normal |  |  |  | Abnormal |  |  | Annex |  | UEL<80% |  |  | UEL>80% |  |  | UEL<80% |  |  |  | UEL>80% |  |  |
|  | Gas or liquid |  | None |  |  |  | None |  |  | E.2 |  | Not applicable |  |  |  |  |  | Not applicable |  |  |  |  |  |  |
|  | Gas |  | None |  |  |  | Limited |  |  | E.3 |  | Air or inert |  |  | Air |  |  | Inert only |  |  |  | <no> |  |  |
|  | Gas |  | Limited |  |  |  | Limited |  |  | E.4 |  | Air or inert |  |  | Air |  |  | <no> |  |  |  | <no> |  |  |
|  | Liquid |  | None |  |  |  | Limited |  |  | E.3 |  | Inert only |  |  | <no> |  |  | Inert only |  |  |  | <no> |  |  |
|  | Liquid |  | Limited |  |  |  | Limited |  |  | E.4 |  | <no> |  |  | <no> |  |  | <no> |  |  |  | <no> |  |  |
|  | <no> means pressurization technique is not acceptable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Internal partitions used to ensure potential ignition sources outside the dilution area (see Annex F): |  |  |  |  |  |  |  |  |  |  |  | Fig. F.1 |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Fig. F.2 |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Fig. F.3 |  |  |  |  |  |  |  |  |  |  |  |
|  | Protective gas inert: |  |  |  |  |  |  | NO |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | YES and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | pressurized enclosure marked in accordance with 18.9 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 35 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  |  | PRESSURIZED APPARATUS WITH AN INTERNAL SOURCE OF RELEASE 6/8 PROTECTIVE GAS AND PRESSURIZING TECHNIQUES 2/3 |  |  |  |  |  | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  | # YES | NO | ENCL. |  |  |
| 10, 13.2 |  |  |  |  | Pressurization with leakage compensation |  |  |  |  |  |  |  |  |  |  |
| 10, 13.2.1 |  |  |  |  | Leakage compensation and no release |  |  |  |  |  |  |  |  |  |  |
| 10, 13.2.2 |  |  |  |  | Leakage compensation and limited release of a gas or liquid |  |  |  |  |  |  |  |  |  |  |
| 10, 13.3 |  |  |  |  | Pressurization with dilution |  |  |  |  |  |  |  |  |  |  |
| 10, 13.3.1 |  |  |  |  | Dilution and no release |  |  |  |  |  |  |  |  |  |  |
| 10, 13.3.2 |  |  |  |  | Dilution and limited release of a gas or vapour |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Leakage compensation and no release |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Protective gas is: |  |  |  |  |  | air |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | inert |  |  |  |  |  |  |  |  |
| ### Leakage compensation and limited release of a gas or liquid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The following requirements are fulfilled: |  |  |  |  |  |  |  |  | protective gas is inert |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | concentration of oxygen in flammable substance does not exceed 2 % (V/V) |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | no normal release (see annex E) of the flammable substance |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | UEL of flammable substance does not exceed 80 % |  |  |  |  |  |
| ### Dilution and no release |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Protective gas is: |  |  |  |  |  | air |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | inert |  |  |  |  |  |  |  |  |
| ### Dilution and limited release of a gas or vapour |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Protective gas is air and: |  |  |  |  |  | flammable substance in the release is diluted to a concentration not exceeding 25 % of the LEL |  |  |  |  |  |  |  |

Sheet 36 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  |  |  | PRESSURIZED APPARATUS WITH AN INTERNAL SOURCE OF RELEASE 7/8 PROTECTIVE GAS AND PRESSURIZING TECHNIQUES 3/3 IGNITION-CAPABLE APPARATUS 1/1 |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  | # YES | NO | ENCL. |  |  |  |
| 10, 13.3.2 |  |  |  |  |  | Dilution and limited release of a gas or vapour (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10, 13.3.3 |  |  |  |  |  | Dilution and limited release of a liquid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10, 14 |  |  |  |  |  | Ignition-capable apparatus |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dilution and limited release of a gas or vapour (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Protective gas is inert and: |  |  |  |  |  |  |  | oxygen in the release is diluted to a concentration not exceeding 2 % (V/V) |  |  |  |  |  |  |  |  |  |  |
|  |  | Flammable substance released from the containment system has an UEL greater than 80 % and: |  |  |  |  |  |  |  |  |  |  | any release is diluted with air to a concentration not exceeding 25 % of the LEL |  |  |  |  |  |  |  |
| ### Dilution and limited release of a liquid |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The protective gas is inert and: |  |  |  |  |  |  |  |  |  | oxygen in the release is diluted to a concentration not exceeding 2 % (V/V) and |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | there is no normal release (see annex E) of the flammable substance |  |  |  |  |  |  |  |  |  |
| Ignition-capable apparatus |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Ignition-capable apparatus is: |  |  |  |  |  |  |  |  |  | electrical |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | flame, ignitor or similar apparatus to ignite a flame |  |  |  |  |  |  |  |  |  |
|  |  |  | The dilution area from the flame does not overlap any other dilution area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The following type(s) of protection for electrical apparatus are applied within the dilution area: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ## Internal release is |  |  |  |  |  |  |  |  |  | Type px, Type py |  |  |  | Type pz |  |  |  |  |  |
|  | abnormal |  |  |  |  |  |  |  |  |  | d, e, i, m, o, q |  |  |  | d, e, i, m, o, q, nA, nC |  |  |  |  |  |
|  | normal |  |  |  |  |  |  |  |  |  | ia |  |  |  | ia |  |  |  |  |  |

Sheet 37 of 56	(IEC 60079-2, 2001-02)

| ## IEC 60079-2 |  |  | PRESSURIZED APPARATUS WITH AN INTERNAL SOURCE OF RELEASE 8/8 INTERNAL HOT SURFACES 1/1 |  |  |  |  |  |  | # APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  | # YES | NO | ENCL. |  |
| 10, 15 |  |  | Internal hot surfaces |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Internal hot surfaces |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Pressurized enclosure contains surface(s) having a temperature which exceeds the ignition temperature of the flammable substance released from the containment system: |  |  |  |  |  |  |  | NO |  |  |  |  |
|  |  |  |  |  |  |  |  |  | YES and |  |  |  |  |
|  |  |  |  |  |  |  |  |  | automatic safety device provided and |  |  |  |  |
|  |  |  |  |  |  |  |  |  | action/operation of automatic safety device in accordance with 11.1.2 b) and table 3 |  |  |  |  |
|  | Additionally: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Protective gas is air: |  |  |  | release of the remaining flammable substance in the containment system does not form a concentration greater than 50 % of the LEL in the vicinity of the hot surface(s) |  |  |  |  |  |  |  |  |
|  | Protective gas is inert: |  |  |  | design and construction of joints of the pressurized enclosure prevent significant mixing of external air with the inert gas (or internal flammable gas or vapour) during the cooling period |  |  |  |  |  |  |  |  |
|  |  |  |  |  | the ingress of external air does not increase the concentration of oxygen to a value greater than 2 % (V/V) |  |  |  |  |  |  |  |  |
|  |  | The pressurized enclosure is marked with a warning stating the delay to be observed between removal of the source of heat within the pressurized enclosure and the opening of the doors or covers. |  |  |  |  |  |  |  |  |  |  |  |
|  | The delay is determined by: |  |  |  |  |  | time taken from the hot surface to cool down below the ignition temperature of the flammable substance from the containment system or |  |  |  |  |  |  |
|  |  |  |  |  |  |  | time to cool down below the temperature class of the pressurized enclosure |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 38 of 56	(IEC 60079-2, 2001-02)

| ## IEC 60079-2 |  |  |  | TYPE VERIFICATION AND TESTS 1/12 |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  | # YES |  | NO |  |  | ENCL. |  |  |
| 16.1 |  |  |  | Maximum overpressure test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.2 |  |  |  | Leakage test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.2.1 |  |  |  | Leakage test (not for static pressurization) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Maximum overpressure test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Maximum overpressure carried out at: |  |  |  |  |  |  |  | 1,5 x maximum overpressure = |  |  |  |  | Pa |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | or |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 200 Pa |  |  |  |  |  |  |  |  |  |  |  |
|  | Pressure applied to: |  |  |  |  | pressurized enclosure and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | associated ducts and their connecting parts |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The pressure was applied for 2 min  10 s. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The test was carried out with satisfactory results since no permanent deformation occurred which would invalidate the type of protection. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Leakage test (not for static pressurization) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | outlet aparture closed |  |  |  |  |  |  |  |  |  | Leakage flow rate measured at the inlet aperture = |  |  |  |  |  |  |  |  |
|  |  | Pressure in pressurized enclosure adjusted to maximum overpressure = |  |  |  |  | Pa |  |  |  |  |  |  |  |  | l /min |  |  |  |  |
|  |  | Leakage flow rate specified by the manufacturer = |  |  |  |  |  |  |  |  | l/min |  |  |  |  |  |  |  |  |  |
|  |  | The test was carried out with satisfactory results since the measured flow rate was not greater than the maximum leakage flow rate specified by the manufacturer. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 39 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | TYPE VERIFICATION AND TESTS 2/12 |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  | # YES | NO |  |  | ENCL. |  |  |  |
| 16.2.2 |  |  |  | Leakage test for static pressurization |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.3 |  |  |  | Purging test for pressurized enclosures with no internal source of release (pressurization technique may be leakage compensation or continuous flow) and filling procedure test for static pressurization |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.3.1 |  |  |  | Purging test for pressurized enclosure where the protective gas is air |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Leakage test for static pressurization |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | aperature(s) closed |  |  |  |  |  | Internal pressure monitored in accordance with 8.7 = |  |  |  |  | h |  |  |  |  |
|  |  | Pressure in pressurized enclosure adjusted to maximum overpressure = |  |  | Pa |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Change of pressure = |  |  |  |  | Pa |  |  |  |  |
|  |  | Minimum overpressure specified by the manufacturer = |  |  |  |  |  |  | Pa |  |  |  |  |  |  |  |  |
|  |  | The test was carried out with satisfactory results since the change of pressure was not greater than the minimum overpressure specified by the manufacturer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Purging test for pressurized enclosure where the protective gas is air |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The pressurized enclosure was prepared for test as described in Annex A. The measurement locations are shown in the annex (es) to this report. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out for the following specific flammable gases: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Density of the heaviest gas is: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Density of the lightest gas is |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 40 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | TYPE VERIFICATION AND TESTS 3/12 |  |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | # YES |  | NO |  |  | ENCL. |  |  |
| 16.3.1 |  |  |  | ### Purging test for pressurized enclosure where the protective gas is air (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Purging test for pressurized enclosure where the protective gas is air (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out for the following single specified gas: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | with a density of: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out to cover all flammable gases |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Pressurized enclosure filled with |  |  |  |  | Single test gas |  | Lightest test gas |  | Heaviest test gas |  |  |  | helium |  | argon |  |  | carbon dioxide |  |
|  |  |  | concentration % (>70 %) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | density ( 10 % of specified gas) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Pressurized enclosure filled with air at purge rate: |  |  |  |  |  |  |  | l/min |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Time taken until test gas concentration was below: |  |  |  |  |  | 25 % of LEL in case of single test gas, |  |  |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 25 % of LEL of lightest test gas, |  |  |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 25 % of LEL of heaviest test gas, |  |  |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 1 % helium, |  |  |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 0,25 % argon, |  |  |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 0,25 % carbon dioxide, |  |  |  |  |  |  | min |  |  |  |  |  |  |
|  |  | Minimum purging duration specified by the manufacturer |  |  |  |  |  |  |  |  |  | min |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out with satisfactory results since the minimum purging duration specified by the manufacturer is not less than the measured purging time(s). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 41 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  |  |  | TYPE VERIFICATION AND TESTS 4/12 |  |  |  |  | # APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  | # YES | NO | ENCL. |  |  |  |
| 16.3.2 |  |  |  |  |  | ### Purging test for pressurized enclosure where the protective gas is inert |  |  |  |  |  |  |  |  |  |  |
| 16.3.3 |  |  |  |  |  | ### Purging test for pressurized enclosure where the protective gas may be either air or an inert gas with a density equal to air 10 % |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Purging test for pressurized enclosure where the protective gas is inert |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The pressurized enclosure was prepared for test as described in Annex A. The measurement locations are shown in the annex (es) to this report. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Enclosure filled initially with air at normal atmospheric pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Inert gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Purginge rate: |  |  |  |  |  | l/min |  |  |  |  |  |  |  |  |  |
|  | Time taken until oxygen concentration did not exceed 2% (V/V) |  |  |  |  |  |  |  |  | min |  |  |  |  |  |  |
|  | Minimum purging duration specified by the manufacturer |  |  |  |  |  |  |  |  | min |  |  |  |  |  |  |
|  |  | Tests were carried out with satisfactory results since the minimum purging duration specified by the manufacturer is not less than the measured purging time(s). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Purging test for pressurized enclosure where the protective gas may be either air or an inert gas with a density equal to air 10 % |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Air and inert gas are permitted as alternative protective gases with the same purging time. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Purging time measured by the method specified in 16.3.1. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 42 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  |  | TYPE VERIFICATION AND TESTS 5/12 |  |  |  |  |  | # APPLIED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  | # YES |  | NO | ENCL. |  |  |
| 16.3.4 |  |  |  |  | Filling procedure test for a pressurized enclosure protected by static pressurization |  |  |  |  |  |  |  |  |  |  |  |
| 16.4 |  |  |  |  | Purging and dilution tests for a pressurized enclosure with an internal source of release |  |  |  |  |  |  |  |  |  |  |  |
| 16.4.1 |  |  |  |  | Test gas |  |  |  |  |  |  |  |  |  |  |  |
| 16.4.2 |  |  |  |  | Pressurized enclosure where the flammable substance has less than 2 % (V/V) oxygen and the protective gas is inert |  |  |  |  |  |  |  |  |  |  |  |
| 16.4.2.1/16.4.2.2 |  |  |  |  | Purging test/dilution test |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Filling procedure test for a pressurized enclosure protected by static pressurization |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Enclosure filled initially with air at normal atmospheric pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Inert gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Apparatus filled with inert gas according to manufacturer's specification |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Test was carried out with satisfactory results since the oxygen concentration did not exceed 1 % (V/V) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Test gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The test gas takes into account both the external gases and the internally released flammable substance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Test gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Purging test/dilution test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Dilution test not required because the flammable substance does not contain more than 2 % (V/V) oxygen |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Purging test carried out in accordance with the test procedure specified in 16.3.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Minimum purge flow rate |  |  |  | l/min |  |  |  |  |  |  |  |  |  |  |
|  |  | Maximum release from containment system |  |  |  |  | l/min |  |  |  |  |  |  |  |  |  |
|  |  | Minimum purge flow rate is not less than the maximum release rate from the containment system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out with satisfactory results since the minimum purging duration specified by the manufacturer is not less than 1,5 times the measured purging time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 43 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  | TYPE VERIFICATION AND TESTS 6/12 |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  | # YES |  |  | NO | ENCL. |  |  |  |  |
| 16.4.3 |  |  | Pressurized enclosure with pressurization by continous flow, containment system with less than 21 % (V/V) oxygen and the protective gas is inert |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.4.3.1 |  |  | Purging test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Purging test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Maximum release rate of the containment system represents the most onerous conditions of release taking into account: |  |  |  |  | position of the releases |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | number of releases |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | nature of releases |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | proximity to potentially ignition-capable apparatus that is outside the dilution area |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Maximum release rate is |  | l/min |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Enclosure was filled with air and air was also injected into the enclosure through the containment system at a flow rate corresponding with the above mentioned release rate |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The supply of protective gas was turned on at the minimum flow rate of |  |  |  |  |  |  |  | l/min |  |  |  |  |  |  |  |
|  |  | Purging time taken until oxygen concentration did not exceed 2% (V/V) |  |  |  |  |  |  |  |  | min |  |  |  |  |  |  |
|  |  | Minimum purging duration specified by the manufacturer |  |  |  |  | min |  |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out with satisfactory results since the minimum purging duration specified by the manufacturer is not less than the measured purging time(s). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 44 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  | TYPE VERIFICATION AND TESTS 7/12 |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  |  | # YES |  |  | NO |  |  | ENCL. |  |  |
| 16.4.3.2 |  |  | Dilution test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Dilution test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Dilution test carried out: |  |  |  |  | immediately after purging test specified in 16.4.3.1 with |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | with protective gas adjusted to minimum flow rate |  |  |  |  |  |  | l/min |  |  |  |  |  |  |
|  |  |  |  |  |  | with oxygen flow rate from containment system specified in 16.4.3.1 |  |  |  |  |  |  | l/min |  |  |  |  |  |  |
|  |  | Oxygen concentration measured during |  |  |  |  |  | min |  |  |  | (at least 30 min) |  |  |  |  |  |  |  |
|  |  | does not exceed 2 % (V/V) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Release into the pressurized enclosure: |  |  |  | quantity of air containing an equivalent of oxygen to that within the containment system |  |  |  |  |  |  |  |  |  | l |  |  |  |  |
|  |  |  |  | and |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | air in accordance with 12.3 |  |  |  |  | l/min |  |  |  |  |  |  |  |  |  |
|  | Concentration of oxygen in the vicinity of ignition-capable apparatus outside the dilution area during the period of release: |  |  |  |  |  |  |  |  3 % (V/V) |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | and < 2 % (V/V) within 30 min.: |  |  |  |  |  |  | min |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 45 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  |  | TYPE VERIFICATION AND TESTS 8/12 |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | # YES |  | NO |  |  | ENCL. |  |  |
| 16.4.4 |  |  |  |  | Pressurized enclosure where the flammable substance is not a liquid, pressurization by continuous flow and the protective gas is air |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.4.4.1 |  |  |  |  | Purging test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Purging test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The pressurized enclosure was prepared for test as described in Annex A. The measurement locations are shown in the annex (es) to this report. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out for the following specific flammable gases: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Density of the heaviest gas: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Density of the lightest gas: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out for the following single specified gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | with a density of: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out to cover all flammable gases |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Pressurized enclosure filled with |  |  |  |  |  | Single test gas |  | Lightest test gas |  | Heaviest test gas |  |  | helium |  |  | argon |  | carbon dioxide |  |
|  |  |  | concentration % (>70 %) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | density ( 10 % of specified gas) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Pressurized enclosure filled with air at purge rate: |  |  |  |  |  |  |  | l/min |  |  |  |  |  |  |  |  |  |  |
|  | In addition: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Maximum release rate of the containment system represents the most onerous conditions of release taking into account: |  |  |  |  |  |  |  | position of the releases |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | number of the releases |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | nature of the releases |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | proximity to potentially ignition-capable apparatus that is outside the dilution area |  |  |  |  |  |  |  |  |  |  |  |

Sheet 46 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | TYPE VERIFICATION AND TESTS 9/12 |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  | # YES |  |  | NO | ENCL. |  |  |  |
| 16.4.4.1 |  |  |  | Purging test (continued) |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.4.4.2 |  |  |  | Dilution test |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Purging test (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Maximum release rate: |  |  | l/min |  |  |  |  |  |  |  |  |  |  |  |
|  | Time taken until test gas concentration was below: |  |  |  |  | 25 % of LEL in case of single test gas, |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  | 25 % of LEL of lightest test gas, |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  | 25 % of LEL of heaviest test gas, |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  | 1 % helium, |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  | 0,25 % argon, |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  | 0,25 % carbon dioxide, |  |  |  | min |  |  |  |  |  |  |
|  | Minimum purging duration specified by the manufacturer |  |  |  |  |  | min |  |  |  |  |  |  |  |  |  |
|  |  | Tests were carried out with satisfactory results since the minimum purging duration specified by the manufacturer is not less than the measured purging time(s). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Dilution test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Dilution test carried out: |  |  |  |  | immediately after purging test specified in 16.4.4.1 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | with minimum dilution flow rate, |  |  |  | l/min |  |  |  |  |  |  |
|  |  |  |  |  |  | and test gas flow rate from the containment system specified in 16.4.3.1, |  |  |  | l/min |  |  |  |  |  |  |
|  | Test gas concentration during a time period less than 30 min did not exceed: |  |  |  |  | 25 % of LEL in case of single test gas, |  |  |  |  | min |  |  |  |  |  |
|  |  |  |  |  |  | 25 % of LEL of lightest test gas, |  |  |  |  | min |  |  |  |  |  |
|  |  |  |  |  |  | 25 % of LEL of heaviest test gas, |  |  |  |  | min |  |  |  |  |  |
|  |  |  |  |  |  | 1 % helium, |  |  |  |  | min |  |  |  |  |  |
|  |  |  |  |  |  | 0,25 % argon, |  |  |  |  | min |  |  |  |  |  |
|  |  |  |  |  |  | 0,25 % carbon dioxide, |  |  |  |  | min |  |  |  |  |  |

Sheet 47 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  | TYPE VERIFICATION AND TESTS 10/12 |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  | # YES |  | NO |  |  | ENCL. |  |  |
| 16.4.4.2 |  |  | Dilution test (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.5 |  |  | Verification of minimum overpressure |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dilution test (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Release into the pressurized enclosure: |  |  |  | quantity of test gas equivalent to the volume of flammable gas in the containment system together with |  |  |  |  | l |  |  |  |  |  |  |
|  |  |  |  |  | a flow of test gas equivalent to the maximum release of flammable gas in accordance with 12.3 |  |  |  |  | l/min |  |  |  |  |  |  |
|  | During the period of release the concentration of test gas in the vicinity of ignition-capable apparatus outside the dilution area was: |  |  |  | < 50 % of LEL in case of single test gas, |  |  |  |  | % |  |  |  |  |  |  |
|  |  |  |  |  | < 50 % of LEL of lightest test gas, |  |  |  |  | % |  |  |  |  |  |  |
|  |  |  |  |  | < 50 % of LEL of heaviest test gas, |  |  |  |  | % |  |  |  |  |  |  |
|  |  |  |  |  | < 2 % helium, |  |  |  |  | % |  |  |  |  |  |  |
|  |  |  |  |  | < 0,5 % argon, |  |  |  |  | % |  |  |  |  |  |  |
|  |  |  |  |  | < 0,5 % carbon dioxide, |  |  |  |  | % |  |  |  |  |  |  |
|  | The concentration of test gas in the vicinity of ignition-capable apparatus outside the dilution area was, within 30 min, reduced to: |  |  |  |  25 % of LEL in case of single test gas, |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  25 % of LEL of lightest test gas, |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  25 % of LEL of heaviest test gas, |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  1 % helium, |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  0,25 % argon, |  |  |  |  | min |  |  |  |  |  |  |
|  |  |  |  |  |  0,25 % carbon dioxide, |  |  |  |  | min |  |  |  |  |  |  |
| ### Verification of minimum overpressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Pressure measured at points where: |  |  |  |  |  | leakage is likely to occur |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | the lowest pressure will occur |  |  |  |  |  |  |  |  |  |
|  | Pressurized enclosure supplied with protective gas: |  |  |  |  |  | at minimum overpressure |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | at minimum flowrate |  |  |  |  |  |  |  |  |  |
|  | Minimum overpressure: |  |  |  |  | Pa |  | for type px or py |  |  |  |  | (at least 50 Pa) |  |  |  |
|  |  |  |  |  |  | Pa |  | for type pz |  |  |  |  | (at least 25 Pa) |  |  |  |

Sheet 48 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | TYPE VERIFICATION AND TESTS 11/12 |  |  |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  | # YES | NO |  |  |  |  |  |  | ENCL. |  |  |  |
| 16.5 |  |  |  | Verification of minimum overpressure(continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.6 |  |  |  | Tests for an infallible containment system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.6.1 |  |  |  | Overpressure test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.6.2 |  |  |  | Infallibility test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verification of minimum overpressure(continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | For rotating electrical machines: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Minimum overpressure with the machine stopped: |  |  |  |  |  |  | Pa |  |  |  | for type px or py |  |  |  |  |  |  |  |  | (at least 50 Pa) |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Pa |  |  |  | for type pz |  |  |  |  |  |  |  |  | (at least 25 Pa) |  |  |  |  |  |
|  | Minimum overpressure at running max. rated speed: |  |  |  |  |  |  | Pa |  |  |  |  | for type px or py |  |  |  |  |  |  |  |  | (at least 50 Pa) |  |  |  |  |
|  |  |  |  |  |  |  |  | Pa |  |  |  |  | for type pz |  |  |  |  |  |  |  |  | (at least 25 Pa) |  |  |  |  |
| ### Overpressure test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The test pressure achieved the maximum pressure within 5 s and applied for a period of 2 min  10 s. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Maximum internal overpressure for normal service |  |  |  |  |  |  |  | Pa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Pressure test carried out at: |  |  |  |  |  | 5 x maximum overpressure, |  |  |  |  |  |  | Pa |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | minimum overpressure, |  |  |  |  |  |  | 1000 Pa |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Overpressure test was carried out with satisfactory result since no permanent deformation occurred and the infallibility test in 16.6.2 was passed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Infallibility test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Containment system: |  |  |  | surrounded by helium at a pressure equal to the maximum specified pressure and |  |  |  |  |  |  |  |  |  |  | Pa |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | evacuated to 0,1 bar or better |  |  |  |  |  |  |  |  |  |  | Pa |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | located in vacuum chamber at 0,1 bar or better |  |  |  |  |  |  |  |  |  |  | Pa |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | connected to helium supply at a pressure equal to the maximum specified pressure |  |  |  |  |  |  |  |  |  |  | Pa |  |  |  |  |  |  |  |  |  |
|  |  | Test was been carried out with satisfactory results since an absolute pressure of 0,1 Pa could be maintained with the evacuating system operating. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 49 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  |  | TYPE VERIFICATION AND TESTS 12/12 |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  | # YES |  |  | NO |  | ENCL. |  |  |  |
| 16.7 |  |  |  |  | Overpressure test for a containment system with a limited release |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16.8.1 to 16.8.4 |  |  |  |  | Verifying ability of the pressurized enclosure to limit internal pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Overpressure test for a containment system with a limited release |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Maximum internal overpressure |  |  |  |  |  | Pa |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Test pressure applied to the containment system for 2 min  10 s: |  |  |  |  |  | 1,5 x max. internal overpressure of |  |  |  |  | Pa |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | or minimum pressure of |  |  |  |  | 200 Pa |  |  |  |  |  |  |  |
|  |  | Test was carried out with satisfactory results since no permanent deformation occurred. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Verifying ability of the pressurized enclosure to limit internal pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Enclosure is designed for use: |  |  |  |  |  |  | with compressed air |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | where leakage, vents, or pressurized relief devices are relied upon to limit the maximum overpressure when a regulator fails |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Specified maximum overpressure |  |  |  |  |  |  | kPa |  |  |  |  |  |  |  |  |  |  |
|  | Pressurization system tested: |  |  |  |  |  |  | at maximum rated supply pressure of or |  |  |  |  |  |  | Pa |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 690 kPa |  |  |  |  |
|  |  |  |  |  |  |  |  | at minimum pressure of |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | with regulator in the pressurization system by-passed to simulate failure of the regulator and |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | with all openings, excluding vents and pressure relief devices closed |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The test was carried out with satisfactory results since the measured internal pressure did not exceed the specified maximum overpressure. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 50 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | ROUTINE TESTS 1/1 | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS | # YES | NO | ENCL. |  |  |
| 17.1 |  |  |  | Functional test |  |  |  |  |  |
| 17.2 |  |  |  | Leakage test |  |  |  |  |  |
| 17.3 |  |  |  | Tests for an infallable containment system |  |  |  |  |  |
| 17.4 |  |  |  | Test for a containment system with a limited release |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |
| ### Functional test |  |  |  |  |  |  |  |  |  |
|  |  | The performance of the safety devices verified |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |
| ### Leakage test |  |  |  |  |  |  |  |  |  |
|  |  | Leakage of protection gas tested as specified in 16.2 |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |
| ### Test for an infallible containment system |  |  |  |  |  |  |  |  |  |
|  |  | Infallible containment system tested as specified in 16.6 |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |
| ### Test for a containment system with a limited release |  |  |  |  |  |  |  |  |  |
|  |  | Containment system tested as specified in 16.7 |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |

Sheet 51 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | MARKING 1/4 | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS | # YES | NO | ENCL. |  |  |
| 18.1 |  |  |  | According to IEC 60079-0 |  |  |  |  |  |
| 18.2 |  |  |  | Warning markings |  |  |  |  |  |
| 18.3 |  |  |  | Supplementary information |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |
| ### According to IEC 60079-0 |  |  |  |  |  |  |  |  |  |
|  |  | Enclosure marked in accordance with the requirements of IEC 60079-0 |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |
| ### Warning markings |  |  |  |  |  |  |  |  |  |
|  |  | Text following the word "WARNING replaced by technically equivalent text |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |
| ### Supplementary information |  |  |  |  |  |  |  |  |  |
|  |  | Required type of protection marking px, py or pz |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |

Sheet 52 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  | MARKING 2/4 |  |  | # APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | REQUIREMENTS |  |  | # YES | NO | ENCL. |  |
| 18.3 |  |  | Supplementary information (continued) |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |
| Supplementary information (continued) |  |  |  |  |  |  |  |  |  |
|  | Minimum quantity of protective gas required to purge the enclosure specified by: |  |  |  | minimum purging flow rate of protective gas; and |  |  |  |  |
|  |  |  |  |  | minimum purging duration and |  |  |  |  |
|  |  |  |  |  | minimum additional purging duration per unit volume of additional ducting (where appropriate) |  |  |  |  |
|  |  | Type of protective gas if other than air |  |  |  |  |  |  |  |
|  |  | Minimum and maximum overpressure |  |  |  |  |  |  |  |
|  |  | Minimum flow rate of protective gas |  |  |  |  |  |  |  |
|  |  | Minimum and maximum supply pressure to the pressurization system |  |  |  |  |  |  |  |
|  |  | Maximum leakage rate from the pressurized enclosure |  |  |  |  |  |  |  |
|  |  | Special temperature (range) for the protective gas at the inlet to the pressurized enclosure when specified by the manufacturer |  |  |  |  |  |  |  |
|  |  | Point(s) at which the pressure is to be monitored unless indicated in the relevant documentation |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |

Sheet 53 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | MARKING 3/4 | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS | # YES | NO | ENCL. |  |  |
| 18.4 |  |  |  | Additional marking if containment system provided |  |  |  |  |  |
| 18.5 |  |  |  | Static pressurization |  |  |  |  |  |
| 18.6 |  |  |  | Separate certification |  |  |  |  |  |
| 18.7 |  |  |  | Valve(s) |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |
| ### Additional marking if containment system provided |  |  |  |  |  |  |  |  |  |
|  | Maximum inlet pressure to the containment system |  |  |  |  |  |  |  |  |
|  | Maximum flow rate into the containment system |  |  |  |  |  |  |  |  |
|  | Restriction that the flammable substance oxygen concentration must not exceed 2 % |  |  |  |  |  |  |  |  |
|  | Restriction that the flammable substance shall not have a UEL higher than 80 % |  |  |  |  |  |  |  |  |
| ### Static pressurization |  |  |  |  |  |  |  |  |  |
|  | Warning label provided |  |  |  |  |  |  |  |  |
| Separate certification |  |  |  |  |  |  |  |  |  |
|  | Separately certified pressurization systems and associated safety devices are marked [Ex p] |  |  |  |  |  |  |  |  |
| Valve(s) |  |  |  |  |  |  |  |  |  |
|  | Warning label provided as required by 7.9 d) 3) |  |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |

Sheet 54 of 56	(IEC 60079-2, 2001-02)

| IEC 60079-2 |  |  |  | MARKING 4/4 |  |  |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  | # YES |  |  | NO | ENCL. |  |  |
| 18.8 |  |  |  | Limited pressure |  |  |  |  |  |  |  |  |  |  |  |
| 18.9 |  |  |  | Inert gas as protective gas |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Limited pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Instructions require the user to limit the pressure: |  |  |  |  |  | YES |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | NO |  |  |  |  |  |  |  |
|  |  | If yes: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The maximum operating pressure is marked: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | and the instructions contain either of the following: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Requirements for the user to install a protective gas supply that will not exceed the maximum operating pressure of the enclosure under single-fault conditions and the fault is self-revealing and |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | proteprotection is either: |  |  |  | a redundant regulator or |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | an external pressure relief valve that is capable of handling the maximum flow rate |  |  |  |  |  |  |  |  |  |
|  |  | or |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Requirements for the user to use only a blower system and not compressed air for the protective gas supply |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ### Inert gas as protective gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Warning label provided |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 55 of 56	(IEC 60079-2, 2001-02)

| IEC 61241-4 |  | COMMENTS |  |  |
| --- | --- | --- | --- | --- |
| #### Clause |  |  | Page |  |

Sheet 56 of 56	(IEC 60079-2, 2001-02)